## FLOW CHART
Heat Reuse Economics Tool: Input and Calculation Flow
Step # | Action | Actor | Shown at Dictionary Lines | Flow Diagram Box
1 | Input Site Introductory Information | Client | 3 - 30 | Site
2 | Input Data Hall and Computer information | Client | 31 - 42 | Data Cooling
3 | Input Power requirements data | Client | 43 - 72 | Power
4 | Input Mechanical Operating Parameters | Client | 73 - 118 | Performance
5 | Estimate all business operational costs for one standard year | Client | 184 - 201 | Operations
6 | Estimate business operational BENEFITS to Offtaker for one year | Client | 119 - 132 | Offtaker
7 | Estimate business operational BENEFITS to Tenant for one year | Client | 133 - 143 | Tenant
8 | Estimate business operational BENEFITS to Owner for one year | Client | 147 - 158 | Owner
9 | Calculate Energy and Exchange for one standard year | Engine |  | Opex
10 | Calculate Benefits from all "one-time" Incentives, Offsets, etc. | Client |  | Offsets
11 | Determine figures regarding finance; "Discount rate", time, etc. | Client |  | Finance
12 | Enter estimates for Program, Project & Construction costs | Clt. / Eng. | 158 - 183 | Install
13 | Calculate Initial Costs of building the Heat Reuse Project | Engine |  | Capex
14 | Calculate Project Financial Situation: NPV, IRR, ROI, etc. | Engine | 203- - 212 | Returns
A FEW BASIC CONVENTIONS WITHIN THE WORKBOOK
This worksheet describes the general flow of the information, and where to find it in the Data DICTIONARY
"Client" == The persons who are entering the data in the "TOOL", for whichever reason
"Owner" == The entity who is the principal owner of the data centre facility
"Tenant" == Is the entity who will be performing computing at the site (may or not be different than Owner)
"Offtaker" == The principal entity responsible for offtaking and employing the heat, OR for delivering it to others
"Engine" == The "behind the scenes" computing; unobvious to Clients and "others".
The sheet "INSTALLED SYSTEMS DATABASE" is a COMMUNICATIONS tool, to describe "most" data to stakeholders
The sheet "Data DICTIONARY" is the keystone to the work; all definitions are based here, NOT visible or open to Clients, etc.
The sheets "Methods" and "Clarifications" will grow to include full information backgrounds behind the required entries
The sheet "INSTRUCTIONS" does not yet exist, and will contain a step-by-step path for Clients to use this tool system
The sheet "Data TABLE" is hidden and incomplete; This will be the master page which is the record of all data, past and future. It will be composed of items described at columns "D" and "G" on the "Data DICTIONARY" page.
| CELLS intended for CLIENT INPUT, regardless of which sheet, are white with borders: |  | like this
Tabs intended for Client input are (at this time) shaded orange
Almost all other cells, and some sheets completely, are locked. Put all feedback, etc. in boxes provided (see below).
NOTES BETWEEN DEVELOPERS ARE IN BOXES LIKE THIS - THEY WILL BE TAKEN DOWN LATER
S48
Site
Public Record data for the Data Center Location. Distinguishes Owner and Tenant (if different), indicates precise locations, and general size of the project and the size of the Computer, if known (may be supercomputer)
Data Cooling
Which methods are used to cool the data (Rack Door, Immersion, Cold Plate, Direct-to-chip). It may occur in later iterations of the tool that the outlet temperatures of the various methods can impact the viability of the project.
Operations
What are the costs associated with operating the system?
Performance
The fundamental data for the mechanical operating equipment, to determine the effectiveness and efficiency of the intended installation
Power
All aspects konwn about the site power, including secondary sources and alternates. The type of source for each is recorded, and the rates (this might need to be oversimplified) for each.
Offtaker
Benefits specific to the entity which takes the heat for having the System in place, instead of other Heat Sources
Tenant
Benefits specific to the Data Centre Tenant, from having this system in place, opposed to a non-Heat Reuse environment
Owner
Benefits to the Owner derived from the installation and operation of the System
OpEx
Calculations from all ONGOING benefits and all ONGOING costs involved in the operation of the System
Offsets
All of the "ONE-TIME" bonuses, rebates, incentives, discounts, of all kinds that offset the cost of INSTALLING the System
Finance
As projected by the developers of the project, finance costs and amortization period
Install
Project costs, beginning at the onset of Project Planning, including costs for all permanent equipment, infrastructure and devices.
CapEx
The summation of the costs to build the Project.
Returns
Accounting for all knowable OpeEx and CapEx figures: All of the output of the tool. Includes ROI, NPV, IRR, other metrics

## REDFISH
Redfish Items from OCP Hardware Management for Liquid Cooling
ID | Name | Schema | Property | Type | Comments | DCIM TF ToDo | 2023.1 (R1.0) | Status
RF1 | Equipment type should contain "CDU" not "RackCDU" to cover all CDUs regardless of physical location | CoolingUnit | EquipmentType | Change Enum value | what about other CDUs like embedded in the immersion tank? | More Enums not less. "RackCDU", "CDU" | T | Done
RF2 | Sensors on Server for Flow rate |  |  |  | Flow rate is OK, could be multiple sensors per chassis | Sensor Reading Types added: "LiquidFlow": "Liquid flow (L/s).", | T | Done
"LiquidFlowLPM": "Liquid flow (L/min)."
RF2.1 | Sensors on Server for leak detection |  |  |  | Binary/Analogue(rope/float)/presence&function | covered by sub-resource: "/redfish/v1/Chassis/{ChassisId}/ThermalSubsystem/LeakDetection" | T | Done
RF2.2 | ThermalMetrics; how to represent multiple sensors for temp, flow rate, etc |  |  |  | ThermalMetrics (from chassis) has multiple-temps, singular flow-rate, etc | Partial - Some metrics available | T | Done
RF2.3 | ThermalMetrics; how to represent multiple sensors for temp, flow rate, etc | ThermalMetrics | Flow Rate (array) | Additional array of values on ThermalMetrics | ThermalMetrics expansion for multiple flow rates, pressures, anything else? | Extend ThermalMetrics sensor collections | F | TBD
RF3 | Control on Server for Flow rate (future as hardware does not exist for this) |  |  |  | Covered by flow control | Chassis->Controls (excerpt in LoopConnection) | T | Done
RF7 | Service links - how to manage relationship of Servers to LC infra (CDU); CooledBy? | Chassis |  | Dependency Tracking | Links back to ThermalDomain (modelled on PowerDistribution) | 1) ConnectedCoolingLoops (direct) or 2) CooledBy (both from chassis) | F | DMTF
RF8 | Chassis Type for Manifold; Manifold needs a physical representation | Chassis | ChassisType | New Enum value | Manifold distributes coolant on Cold Plate | Add ChassisType = 'Manifold' to Chassis resource; (FUTURE) cooling unit for distribution | F | DMTF
RF9 | Manifold or Door HX may have an external leak sensor associated with it. | CoolingUnit | Sensors |  | Mockup required to show external leak detector associated with a chassis (rack or manifold or CDU or etc) | Mick to provide physical model. | F | Pending
RF9.1 | Leak detection; binary detector and analog (depth or positional along rope) | CoolingUnit | Sensors |  | Need to support leak detection | Supported; analog leak detectors are sensors | T | Done
RF10 | Sensor is associated with a parent, but physically separate. Do we have a chassis for a sensor? | Chassis | Sensor |  | Standalone networked sensors (e.g. IOT) or dependent external sensor | Covered with ChassisType enum for containment (enclosure, module) | T | Done
Ambient temp covered, can we cover leak detection? Yes
RF11 | Manifold type should be added to CoolingUnit types | CoolingUnit | EquipmentType | New Enum value | Manifold | Add the enum; ON HOLD; no "smarts" in a manifold | F | On hold
RF12 | Documentation link; link to a BIM model for the CoolingUnit | CoolingUnit | Link |  | How do we provide a consistent link type for documentation or schematics (OCP BIM) file(s)? | URI links exist; e.g. webUI. How do we do a link to a local file (Served by redfish service) or a redirect with key to a CMS that hosts the file. | F | DMTF
Link from the chassis of the cooling unit
Phase 1 - Present the link (URL) to the BIM model (client can access it or not).
Phase 2 - Local storage of the BIM model for Redfish client access and consumption
|  | CoolingUnit | EquipmentType | New Enum value | Is "Other" a viable interim solution? | Can we add "Other" to represent these other cooling units? Best way? | F | DMTF says no
RF13 | Pump as standalone unit in liquid cooling chain. I.e. Heat re-use distribution pump | CoolingUnit | EquipmentType | New Enum value | Pump; not standalone resource, currently only a linked sub-resource | Add the enum; on-hold; Pump | F | On hold
RF14 | Tank as standalone unit in liquid cooling chain. I.e. Storage/Buffer tank | CoolingUnit | EquipmentType | New Enum value | Reservior; not standalone resource, currently only a linked sub-resource | Add the enum; on-hold; Reservior | F | On hold
| Filter | CoolingUnit | EquipmentType | New Enum value | Filter; not standalone resource, currently only a linked sub-resource | Add the enum; Filter; are filters a sub-resource and not a standalone CoolingUnit? | F | On hold
RF15 | Heat Pump as standalone unit in liquid cooling chain. I.e. Heat re-use distribution heat pump | CoolingUnit | EquipmentType | New Enum value | Heat Pump. Heat pump adds energy to output to maintain a consistent fluid temp in heat-re-use. | Use "HeatExchanger"; will revisit if standalone category is desired for HeatPump | T | Done
RF17 | Computed sensor; Heat (power) in joules which is a function of fluid temp, fluid properties and flow rate | Sensor | ThermalPower | Kilowatts | Heat removal (Watts from joules). Calculated dynamically from other sensors | Use Kilowatts from testing methodology (At specified ambient) | F
RF18 | Expected consumption/Future consumption; consumer sets an absolute or delta value of future consumption based on demand. I.e. This is what I can consume if you can provide it. | Sensor | Computed | Computed Sensor | Future requirement; how would we represent this in schema? | Computed sensors would expose this. | T | Done
RF19 | Heat loss to environment; the max amount (specification) of heat loss during operation to the ambient environment. I.e. Due to insulation, etc | CoolingUnit | ThermalLoss | Joules/Kilojoules | A property that conveys the expected (specification max) heat loss to the environment during operation. | Kilowatts is Immersion unit; published from testing methodology in Immersion. Use a static attribute to represent this. | F | DMTF
RF20 | Heat loss; dynamic | CoolingUnit | Sensor | Joules | The calculated loss during operation to the environment. A calculated sensor which may encompass multiple underlying sensors | DEFER; not realistic (sensors not accurate enough); use published figure above. | F | DEFER
RF21 | Door HX; fans collection from CoolingUnit | CoolingUnit | Fans | Collection | A collection of fans used in the active HX operation | Fans collection exists under Chassis. EnvironmentMetrics exposes fan speeds as well. Needs to be shown in mockup. Try this for R1.0 and if too many people complain then link it direct from CoolingUnit resource. | T | Done
RF22 | CoolingUnit; Control Method (ControlMethod); each cooling unit has a RW attribute for the control method | CoolingUnit | ControlMethod | New Enum | Filtered by profile; values: Differential Air Pressure; Differential Coolant Pressure; Outlet Air Temp; Return Coolant Temp; Manual (upstream control/external control) | ControlMethod to be added to CoolingUnit with enums; Further discussion on details req'd | F | TBD
RF22.1 | Control Method for cold plate CDU: Differential Coolant Temp (in/out); External Temp sensors (from BMCs); Manual |  |  |  | Adjunct to parent item RF22.1 | ControlMethod to be added to CoolingUnit with enums; Further discussion on details req'd | F | TBD
RF23 | Smoke/particulate sensors; binary and analog | Sensors | Sensor |  | Support for these sensors, but as parallel to Fire Control system | Now: True/False later analog (what units?) | F
RF24 | ACF; external ambient temp/hum sensor | Chassis | Sensor |  | See RF10 | See above sensor with chassis | T | Done
RF25 | ACF: pipework sensors; fluid temp, flow rate, pressure | CoolingLoop | Sensor |  | Also need chassis for sensor (see RF10) | See above | T | Done
RF26 | ACF: pipework actuators; flow rate, emergency cutoff | CoolingLoop | Control |  |  | Is the emergency cutoff value==Supply valve? Ask the community | T | Done
RF27 | Damper position sensor; binary or analog | CoolingUnit | Sensor |  | A sensor indicating current damper position (open/closed or %) | Covered by percent sensor | T | Done
RF28 | Pump sensors; Speed, Flow Valve position | Pump | Sensor |  | Profile; pump controls for CDU are internal controlled and should not be exposed to Redfish | Covered by pump controls | T | Done
RF29 | CoolingUnit; CountryOfOrigin | CoolingUnit | CountryOfOrigin | New attr | Add new attribute "CountryOfOrigin"; Shortform locale: au,us,gb, sg, etc. ISO 3166-1 alpha-2
Feedback:
CoolingUnit; EquipmentType does not need “RackCDU” as self-evident from containment relationship (parent = rack vs parent = facility), need to change description for “CDU” to remove ‘free-standing’.
Location example should include rack since it’s a rack CDU. I.e "Location": {
"Placement": {
"Row": "North 1",
“Rack”: “Rack #4”
}
Example response for Environment metrics should reflect cooling environments; CDU: supply/return temps for fws/tcs plus flow rates
FilterType is missing definition
Rope style (distance from x leak detection). Discrete sensor indicates leak, plus analog sensor to indicates distance along rope that leak was detected at.
Non-discrete (standard sensor) to be part of leak detection
Confirm coolingloop can have sensors for inline sensors as well as on coolingconnection.

## ENQUIRY - MECHANICAL
FALSE
Initial Enquiry for R.o.M. Size and Cost
[9 empty] | 👈🏻 | [5 empty] | Typical Flow Range is up to 675 gpm
[10 empty] | FLOW | MPS |  |  | Typical Flow Range is 700 to 2000 gpm | Typical Flow Range is 225 to 675 gpm
Enter IT Power to be harvested |  | 3 | Anticipated Amount of Data Energy Available for Reuse | [6 empty] | 275 | 4 | 6 |  | Typical Flow Range is 700 to 2000 gpm | Typical Flow Range is 450 to 1350 gpm
Enter Required T1 (to IT) |  | 97 | Temperature Required of Medium to IT Equipment | [6 empty] | 600 | 6 | 8 |  | Typical Flow Range is 700 to 2000 gpm | Typical Flow Range is 700 to 2000 gpm
Enter Flow Rate for IT Cooling Medium |  | 750 | Typical Flow Range is 700 to 2000 gpm | [6 empty] | 1100 | 8 | 10 |  | Typical Flow Range is 1150 to 3300 gpm | Typical Flow Range is 900 to 2700 gpm
Enter Target HRE |  | 0.95 | What efficiency is being targeted? (Not including deductions for load fluctuation) | [6 empty] | 1700 | 10 | 12 |  | Typical Flow Range is 1150 to 3300 gpm | Typical Flow Range is 1150 to 3300 gpm
Enter HX Approach |  | 3.5 | Designed difference between "Return from IT" and "Supply to Heat" | [6 empty] | 2400 | 12 | 14 |  | 0
Enter Flow Rate for Heat Medium |  | 675 | Typical Flow Range is 700 to 2000 gpm | [6 empty] | 3300 | 14 | 16
[10 empty] | 4300 | 16 | 18
Medium Returning From IT (T2) |  | 124.2971 | The temperature of the IT cooling medium as it returns to the Heat Exchanger | [6 empty] | 5000 | 16 | 20
Supply to Heat Consumer (T3) |  | 120.7971 | [11 empty] | Please select a lower "Flow for Heat"; T4 is too high
Medium Returning From Consumer (T4) |  | 91.9835 | Temperature of medium returning from the Heat System | [7 empty] | DT10 | DT30
[10 empty] | 1MW | 675 | 225
dt for IT Medium |  | 27.2971 | Consider whether this is a viable possibility in the IT system | [6 empty] | 2MW | 1350 | 450
dt for Heating Medium |  | 28.8136 | [7 empty] | 3 | 2000 | 700
[10 empty] | 4 | 2700 | 900
Pipe Size for IT Cooling |  | 8 | [7 empty] | 5 | 3300 | 1150
Pipe Size for Heating |  | 8
Fake HX Factors
Order of Magnitude Pricing: |  |  | ALL THESE FIGURES ARE FOR DEMONSTRATION ONLY | [6 empty] | 0.58333
= HX + Pipe, + (Valve & Fittings)
Heat Exchanger = | 89142.8571 |  | Size as per E6, factored by E9 | [6 empty] | Fake HX Costs
Pumps = |  |  | Determination for "Head" requirement TBD | See "Space and Pipe"
Pipe & Ftgs, etc. = | 34133.5532 |  | Size as per E19 & E20, Length as per " Footprint " | [6 empty] | MW
Valves, etc. = | 7447.04 |  | Size to match pipe (control valve one size smaller) | [6 empty] | 0.5 | 16000
Instruments, others = | 30000 |  | Standard Figures for all systems | [6 empty] | 0.75 | 18000
[10 empty] | 1 | 21000
Initial Estimate : | 160723.4503 |  | First Guess of installation costs, based only on physical attributes. (so far) | [6 empty] | 1.25 | 26000
[10 empty] | 1.5 | 30000
[10 empty] | 1.75 | 35000
[10 empty] | 2 | 38000
[10 empty] | 2.25 | 41000
[10 empty] | 2.5 | 42000
[10 empty] | 2.75 | 45000
[10 empty] | 3 | 52000
[10 empty] | 3.25 | 58000
[10 empty] | 3.5 | 61000
[10 empty] | 3.75 | 65000
[10 empty] | 4 | 70000
[10 empty] | 4.25 | 73000
[10 empty] | 4.5 | 77000
[10 empty] | 4.75 | 81000
[10 empty] | 5 | 85000
Imaginary Room Size
"L"
[10 empty] | 1 | 8 | 56 | 22.4499
[10 empty] | 2 | 10 | 63 | 23.8118
[10 empty] | 3 | 12 | 99 | 29.8496
[10 empty] | 5 | 16 | 187 | 41.0244
Fake Valve + Fitting Costs
[5 empty] | 4 | 507 | 10.5561 | 48.0293 |  | 4 | 3549
[5 empty] | 6 | 828 | 21.0309 | 39.3707 |  | 6 | 5796
[5 empty] | 8 | 1277 | 34.2968 | 37.2338 |  | 8 | 8939
[5 empty] | 10 | 1873 | 50.1187 | 37.3713 |  | 10 | 13111
[5 empty] | 12 | 2532 | 68.3295 | 37.0557 |  | 12 | 17724
[5 empty] | 14 | 4870 | 88.801 | 54.8417 |  | 14 | 34090
[5 empty] | 16 | 4870 | 111.4305 | 43.7044 |  | 16 | 34090
Fake pipe per foot
[5 empty] | 4 | 206 |  |  |  | 4 | 20.6
[5 empty] | 6 | 384 |  |  |  | 6 | 38.4
[5 empty] | 8 | 642 |  |  |  | 8 | 64.2
[5 empty] | 10 | 910 |  |  |  | 10 | 91
[5 empty] | 12 | 1226 |  |  |  | 12 | 122.6
[5 empty] | 14 | 2400 |  |  |  | 14 | 240
[5 empty] | 16 | 2500 |  |  |  | 16 | 250
[10 empty] | L = | 29.8496
[10 empty] | PF1 = | 1916.3458
[10 empty] | PF2 = | 1916.3458
[10 empty] | VF1 = | 8939
[10 empty] | VF2 = | 8939
thel4stW0RD

## Enquiry - HRE (hidden)
Tiny Sample from (future) "CLIENT INPUT" Pages
THESE ARE LIVE
What is the rated temperature of cooling medium to the IT Equipment? (T1) | 97 | ºC
What is the rated temperature of cooling medium returning from the IT Equipment? (T2) | 124.2971 | ºC
What is the rated temperature of medium to the Heat Offtaker? (T3) | 120.7971 | ºC
What is the rated temperature of medium returning from the Heat Offtaker? (T4) | 91.9835 | ºC
What is the flow rate of the medium to the IT Equipment? (F1) | 750 | LPM
What is the flow rate of the medium to the Heat Offtaker? (F2) | 675 | LPM
Your HRE (Heat Reuse Effectiveness) is: | 0.95
Your Total Heat Available To Be Reused is: | 1426.5882 | kW
Go To Instrument Page
AB39

## HX (hidden)
MW | Price
0.5 | 16000
0.75 | 18000
1 | 21000
1.25 | 26000
1.5 | 30000
1.75 | 35000
2 | 38000
2.25 | 41000
2.5 | 42000
2.75 | 45000
3 | 52000
3.25 | 58000
3.5 | 61000
3.75 | 65000
4 | 70000
4.25 | 73000
4.5 | 77000
4.75 | 81000
5 | 85000

## INPUT - Fluctuations
Fluctuation Factors Daily or seasonal variability of heat supply and demand
| For Data Centre Computing Operation: If the data operations has a daily usage or loading cycle, estimate the hourly level of compute as compared to fully loaded |  |  |  | For Heat Offtaker Operation: If the Offtaker's operations has a daily usage or loading cycle, estimate the typical hourly level of Heat Use as compared to fully loaded
| For Data Centre Computing Operation: If the data operations has an annual usage or loading cycle, estimate the monthly level of compute as compared to fully loaded |  |  |  | For Heat Offtaker Operation: If the Offtaker's operations has an annual usage or loading cycle, estimate the monthly level of Heat Use as compared to fully loaded
| Percentage of data power in operation: |  |  |  | Percentage of captured heat reused:
| Daily Fluctuation |  | Seasonal Fluctuation |  | Daily Fluctuation |  | Seasonal Fluctuation
| 0:00 | 90% | January | 100% | 0:00 | 100% | January | 100%
| 1:00 | 77.5% | February | 100% | 1:00 | 100% | February | 100%
| 2:00 | 80% | March | 100% | 2:00 | 100% | March | 100%
| 3:00 | 100% | April | 100% | 3:00 | 100% | April | 100%
| 4:00 | 100% | May | 100% | 4:00 | 100% | May | 100%
| 5:00 | 100% | June | 100% | 5:00 | 100% | June | 50%
| 6:00 | 100% | July | 100% | 6:00 | 100% | July | 70%
| 7:00 | 100% | August | 100% | 7:00 | 100% | August | 75%
| 8:00 | 100% | September | 95% | 8:00 | 100% | September | 100%
| 9:00 | 100% | October | 100% | 9:00 | 100% | October | 100%
| 10:00 | 50% | November | 100% | 10:00 | 100% | November | 100%
| 11:00 | 100% | December | 100% | 11:00 | 100% | December | 100%
| 12:00 | 100% |  |  | 12:00 | 100%
| 13:00 | 100% |  |  | 13:00 | 100%
| 14:00 | 100% |  |  | 14:00 | 90%
| 15:00 | 100% |  |  | 15:00 | 75%
| 16:00 | 100% |  |  | 16:00 | 75%
| 17:00 | 100% |  |  | 17:00 | 100%
| 18:00 | 100% |  |  | 18:00 | 100% |  | GO SEE CALCULATIONS
| 19:00 | 100% |  |  | 19:00 | 100%
| 20:00 | 100% |  |  | 20:00 | 100%
| 21:00 | 100% |  |  | 21:00 | 100%
| 22:00 | 100% |  |  | 22:00 | 100%
| 23:00 | 100% |  |  | 23:00 | 100%
Factors: |  | 0.95729 |  | 0.99583 |  | 0.975 |  | 0.9125

## INPUT - Financial
Input for Financial Calculations |  |  | WORK IN PROGRESS
IRR = |  | GX |  | Please add ANY comment or feedback in this box.
NPV = | 5908.2822
Where:
NPV = Net Present Value |  | GY
Rt = net revenue (or savings) in period t |  | @ cell
Ct = Annual Operating Costs |  | @ cell
C0 = Initial Capital costs |  | @ cell
r = discount rate |  | EH
t = time period (years) |  | EJ
Where:
ROI = Return on Investment
NPV = - C0
NPV = ∑24_0^𝑡▒(𝑅𝑡 −𝐶𝑡)/((1+𝑟)𝑡) - C0
CAGR = Compound Annual Growth Rate; measures the annual return of an investment over time. Uses starting and ending values to project an estimated annual growth rate.
IRR = Internal Rate of Return; a metric used in finanacial analysis to estmate the profitability of investments. It is the figure that, when used as the "discount rate" in the NPV formula, returns an NPV of zero.
NPV = Net Present Value; a metric used to capture the total value of an investment opportunity. "Today's value of the expected capital costs".
Payback Period = refers to the amount of time it takes to recover the costs of an investment.
ROI = Return on Investment. = a ratio of the gain or cost of an investment to the net returns of the investment
x 100%
𝑅𝑂𝐼= (𝐹𝑉𝐼 −𝐼𝑉𝐼)/(𝐶𝑜𝑠𝑡 𝑜𝑓 𝐼𝑛𝑣𝑒𝑠𝑡𝑚𝑒𝑛𝑡) x 100%

## HRE Calculations
These are the basic data points required for operating performance calculations, and their general locations within the system | This is an example of how they will be used within the "calculating engine" | [5 empty] | Location of the data point in the Database:
[7 empty] | Alias |  | Column
Basic HRE Sample Calculation
HRE = Useful Heat Reused / Total Waste Heat Available
|  | Total Waste Heat Available = | uhr | = | 1426.5882 | kW | uhr | = | BF
|  | Useful Heat Reused = | wha | = | 1355.2588 | kW | wha | = | BE
|  | Offtaker Delta T = | userdt | = | 28.8136 | ºC | userdt | = | CF
|  | IT Delta T = | itdt | = | 27.2971 | ºC | itdt | = | BP
|  | HRE = uhr / wha | = |  | 0.95
|  | SEE ENTRIES FROM "CLIENT INPUT" HERE: |  |  |  | GO TO CLIENT INPUT
|  | T1 |  | = | 97 | ºF | T1 | = | BL
|  | T2 |  | = | 124.2971 | ºF | T2 | = | BO
|  | T3 |  | = | 120.7971 | ºF | T3 | = | CE
|  | T4 |  | = | 91.9835 | ºF | T4 | = | CB
|  | F1 |  | = | 750 | GPM | F1 | = | BU
|  | F2 |  | = | 675 | LPM | F2 | = | CJ
Adjustments for Diversity Factors
Go To Client Input for "Fluctuations"
|  | Data Centre Daily Fluctuation |  |  | 0.95729 |  | itdivrday | = | DH
|  | Data Centre Seasonal Fluctuation |  |  | 0.99583 |  | itdvryr | = | DI
|  | Waste Heat Available, Adjusted for Fluctuations |  |  | 0.9533 |  | whadvr | = | DJ
|  | Offtaker Daily Fluctuation |  |  | 0.975 |  | dvrusrday | = | CY
|  | Offtaker Seasonal Fluctuation |  |  | 0.9125 |  | dvrusryr | = | CZ
|  | Useful Heat Used, Adjusted for Fluctuations |  |  | 0.88969 |  | uhrdvrad | = | BG
|  | HRE, ADJUSTED FOR FLUCTUATIONS |  |  | 0.80573 |  | hredvrad | = | BH
49.1348
|  | 51.8646 |  |  |  | 146.5416
198.129
178.3161
4867518.9491
4624143.0016
Z80

## TEMPORARY MATH PAGE
For PIPE (Called in from "PIPE" page)
| CAPACITY (from client input) | 3
| Length: (based on size of available mechanical space) | 29.8997
| Flow Rate for IT Medium: | 750
| Imputed Pipe Size for IT: | 8
| Price for IT Pipe (per foot): | 285.4
| Total for IT Pipe |  | 17066.7766
| Flow Rate for HEAT Medium: | 675
| Imputed Pipe Size for HEAT: | 8
| Price for HEAT Pipe (per foot): | 285.4
| Total for HEAT Pipe |  | 17066.7766
| Price for PIPE |  | 34133.5532
For HEAT EXCHANGER (Called in from "HX" page)
| CAPACITY FROM CLIENT INPUT: | 3
| APPROACH FROM CLIENT INPUT: | 3.5
ASSUMPTION: "Standard" HX approach is "6ºF", and HX with closer approach is costlier (until complete data is gathered)
| Listed Standard Price |  | 52000
| Price as adjusted for performance |  | 89142.8571
For VALVES (Called in from "VALVE" page)
| Pipe size for IT piping, from ENQUIRY Page | 8
| Pipe size for HEAT piping, from ENQUIRY Page | 8
| Control Valve Size for IT (~line size - 1 size) | 6
| Control Valve Size for HEAT (~line size - 1 size) | 6
| Cost of two stop valves, IT |  | 1465.92
| Cost of two stop valves, HEAT |  | 1465.92
| Cost of one control valve, IT |  | 2257.6
| Cost of one control valve, HEAT |  | 2257.6
| Valve Price |  | 7447.04
Cost of Equipment |  |  |  | € | FF
Heat-exchanging room elements | Costs for the major equipment of Heat Reuse | costmjeq | float | € | FG
Installation Costs | Ancillary Equipment at Owner space | costmneq | float | € | FH
Costs of Controls | the costs of installing the major equipment within the Owners site, exclusice of piping. | cstinslpip | float | € | FI
Electrical Installation | The sum of all electronic monitoring and controlling devices, including one local "PLC" | costcntrl | float | € | FJ
Piping Diameter (IT Side) | The cost for the installation of both power wiring to the system, and conttrols installation and wiring. | cstelcinst | float | mm | FK
Piping Length (IT Side) | The pipe size of the majority of the headers | pipitdia | int | m | FL
Piping Insulation (IT Side) | The total length of Heat Reuse piping on the IT side of the system | pipitlen | int | mm | FM
Cost of Piping on the IT side | Thickness of the pipe insulation | pipitins | int | € | FN
Piping Diameter (Heat Offtaker Side) | The costs of installing the IT Cooling piping | costpipit | float | mm | FU
Piping Length (Heat Offtaker Side) | The pipe size of the majority of the headers | pipusdia | int | m | FV
Piping Insulation (Heat Offtaker Side) | The total length of Heat Reuse piping on the IT side of the system | pipuslen | int | mm | FQ
Cost of piping on the Offtaker Side, within Owner boundary | thickness of the pipe insulation | pipusins | int | € | FR
Valves and Fittings | Cost to install the Offtaker piping, on Owner site | costpipusr | float | € | FS
Valves and Fittings | An estimation of the ancillary piping devices | costvalit | float | € | FT
Cost of Piping | An estimation of the ancillary piping devices | costvalusr | float | € | FO
Ancillary IT Facility Costs | The sum of all the piping installation costs | costpipe | float | € | FP
Civil works associated | Miscellaneous costs to accommodate the system | costanceq | float | € | FW
Weight bearing elements | All cumulative costs to install the infrastructure, NOT within the Owner or Offtaker boundaries | costcvl | float | € | FX
The cost of installing the Heat Reuse System | Facility structural costs | coststct | float | € | FY
What was the cost of the IT facility or data centre? | Costs of installation, incurred at the Owners site | costinst | float | € | FZ
What was the cost of the IT facility or data centre? | What is the reported value of the IT Facility? | costitctr | float | € | FZ
| What is the reported value of the IT Facility? | costitctr | float

## VALVES (hidden)
Pipe Size | Ball Valve | B'Fly Valve | Control Valve | Relief
1/2 | 42.57 |  |  | 281.34
3/4 | 61.44 |  |  | 290.39
1 | 82.7 |  |  | 372.27
1 1/2 | 306.79 |  |  | 943.43
2 | 442.68 |  | 1375.2 | 1311.52
2 1/2 | 834.24 |  | 1390.4
3 | 1200.23 |  | 1405.6
4 |  | 238.47 | 1436
5 |  | 286.02 | 2500
6 |  | 560.2 | 2257.6
8 |  | 732.96 | 2632.8048
10 |  | 1095.97 | 2880.8
12 |  | 1516.22 | 2910.4
14 |  | 2211.59 | 3600 |  | guesses
16 |  | 3356.71 | 4800
18 |  | 4547.71
20 |  | 6790.13
24 |  | 9710.76

## SPACE and PIPE
THIS TABLE IS COURTESY OF THE HEAT REUSE REFERENCE DESIGN TEAM
DC Load | Supply Temp to IT | Return Temp From IT | Flow for IT | Pipe Size, < 7 fps | Supply Temp to Heat | Return Temp from Heat | Flow for Heat | Pipe Size, < 7 fps | Footprint | SQFT/MW |  | DC Load | Supply Temp to IT | Return Temp From IT | Flow | Pipe Size, < 2 Mps | Supply Temp to Heat | Return Temp from Heat | Flow | Pipe Size, < 2 Mps | Footprint | m2/MW
(MW) | (F) | (F) | GPM |  | (F) | (F) | GPM |  | (sq ft) |  |  | (MW) | (C) | (C) | LPM | mm | (C) | (C) | LPM | mm | (sq m)
1 | 80.6 | 88.5 | 891.8 | 8 | 86 | 76 | 712.1 | 8 | 56 | 56 |  | 1 | 27 | 31.3889 | 3375.463 | 200 | 30 | 24.4444 | 2695.2985 | 200 | 5.2 | 5.2 | EUROPEAN SIZES ARE TEMPORARILY HIDDEN
1 | 104 | 112 | 890.7 | 8 | 110 | 100 | 710.8 | 8 | 56 | 56 |  | 1 | 40 | 44.4444 | 3371.2995 | 200 | 43.3333 | 37.7778 | 2690.378 | 200 | 5.2 | 5.2 | BUT WILL BE THE PRIMARY TYPE
1 | 113 | 121 | 890.6 | 8 | 119 | 109 | 710.5 | 8 | 56 | 56 |  | 1 | 45 | 49.4444 | 3370.921 | 200 | 48.3333 | 42.7778 | 2689.2425 | 200 | 5.2 | 5.2 | USED IN THE FINAL TOOL RELEASE
1 | 80.6 | 110.6 | 238.4 | 4 | 88 | 78 | 712 | 8 | 56 | 56 |  | 1 | 27 | 43.6667 | 902.344 | 100 | 31.1111 | 25.5556 | 2694.92 | 200 | 5.2 | 5.2
1 | 104 | 134 | 238.3 | 4 | 112 | 102 | 710.7 | 8 | 56 | 56 |  | 1 | 40 | 56.6667 | 901.9655 | 100 | 44.4444 | 38.8889 | 2689.9995 | 200 | 5.2 | 5.2
1 | 113 | 143 | 238.3 | 4 | 121 | 111 | 710.5 | 8 | 56 | 56 |  | 1 | 45 | 61.6667 | 901.9655 | 100 | 49.4444 | 43.8889 | 2689.2425 | 200 | 5.2 | 5.2
2 | 80.6 | 88.5 | 1783.6 | 10 | 86 | 76 | 1424.2 | 10 | 63 | 31.5 |  | 2 | 27 | 31.3889 | 6750.926 | 250 | 30 | 24.4444 | 5390.597 | 250 | 6 | 3
2 | 104 | 112 | 1781.4 | 10 | 110 | 100 | 1421.6 | 10 | 63 | 31.5 |  | 2 | 40 | 44.4444 | 6742.599 | 250 | 43.3333 | 37.7778 | 5380.756 | 250 | 6 | 3
2 | 113 | 121 | 1781.2 | 10 | 119 | 109 | 1421 | 10 | 63 | 31.5 |  | 2 | 45 | 49.4444 | 6741.842 | 250 | 48.3333 | 42.7778 | 5378.485 | 250 | 6 | 3
2 | 80.6 | 110.6 | 476.8 | 6 | 88 | 78 | 1424 | 10 | 54 | 27 |  | 2 | 27 | 43.6667 | 1804.688 | 160 | 31.1111 | 25.5556 | 5389.84 | 250 | 5 | 2.5
2 | 104 | 134 | 476.6 | 6 | 112 | 102 | 1421.4 | 10 | 54 | 27 |  | 2 | 40 | 56.6667 | 1803.931 | 160 | 44.4444 | 38.8889 | 5379.999 | 250 | 5 | 2.5
2 | 113 | 143 | 476.6 | 6 | 121 | 111 | 1421 | 10 | 54 | 27 |  | 2 | 45 | 61.6667 | 1803.931 | 160 | 49.4444 | 43.8889 | 5378.485 | 250 | 5 | 2.5
3 | 80.6 | 88.5 | 2675.4 | 14 | 86 | 76 | 2136.3 | 12 | 99 | 33 |  | 3 | 27 | 31.3889 | 10126.389 | 350 | 30 | 24.4444 | 8085.8955 | 315 | 9.2 | 3.0667
3 | 104 | 112 | 2672.1 | 14 | 110 | 100 | 2132.5 | 12 | 99 | 33 |  | 3 | 40 | 44.4444 | 10113.8985 | 350 | 43.3333 | 37.7778 | 8071.5125 | 315 | 9.2 | 3.0667
3 | 113 | 121 | 2671.8 | 14 | 119 | 109 | 2131.5 | 12 | 99 | 33 |  | 3 | 45 | 49.4444 | 10112.763 | 350 | 48.3333 | 42.7778 | 8067.7275 | 315 | 9.2 | 3.0667
3 | 80.6 | 110.6 | 715.2 | 8 | 88 | 78 | 2136 | 12 | 72 | 24 |  | 3 | 27 | 43.6667 | 2707.032 | 200 | 31.1111 | 25.5556 | 8084.76 | 315 | 6.7 | 2.2333
3 | 104 | 134 | 714.9 | 8 | 112 | 102 | 2132.1 | 12 | 72 | 24 |  | 3 | 40 | 56.6667 | 2705.8965 | 200 | 44.4444 | 38.8889 | 8069.9985 | 315 | 6.7 | 2.2333
3 | 113 | 143 | 714.9 | 8 | 121 | 111 | 2131.5 | 12 | 72 | 24 |  | 3 | 45 | 61.6667 | 2705.8965 | 200 | 49.4444 | 43.8889 | 8067.7275 | 315 | 6.7 | 2.2333
5 | 80.6 | 88.5 | 4459 | 16 | 86 | 76 | 3560.5 | 16 | 187 | 37.4 |  | 5 | 27 | 31.3889 | 16877.315 | 400 | 30 | 24.4444 | 13476.4925 | 400 | 17.5 | 3.5
5 | 104 | 112 | 4453.5 | 16 | 110 | 100 | 3554 | 16 | 187 | 37.4 |  | 5 | 40 | 44.4444 | 16856.4975 | 400 | 43.3333 | 37.7778 | 13451.89 | 400 | 17.5 | 3.5
5 | 113 | 121 | 4453 | 16 | 119 | 109 | 3552 | 16 | 187 | 37.4 |  | 5 | 45 | 49.4444 | 16854.605 | 400 | 48.3333 | 42.7778 | 13444.32 | 400 | 17.5 | 3.5
5 | 80.6 | 110.6 | 1192 | 10 | 88 | 78 | 3560 | 16 | 90 | 18 |  | 5 | 27 | 43.6667 | 4511.72 | 250 | 31.1111 | 25.5556 | 13474.6 | 400 | 8.4 | 1.68
5 | 104 | 134 | 1191.5 | 10 | 112 | 102 | 3553.5 | 16 | 90 | 18 |  | 5 | 40 | 56.6667 | 4509.8275 | 250 | 44.4444 | 38.8889 | 13449.9975 | 400 | 8.4 | 1.68
5 | 113 | 143 | 1191.5 | 10 | 121 | 111 | 3552.5 | 16 | 90 | 18 |  | 5 | 45 | 61.6667 | 4509.8275 | 250 | 49.4444 | 43.8889 | 13446.2125 | 400 | 8.4 | 1.68
Return to Enquiry - Mechanical
mw | btu | dt | f
5 | 17060708.166 | 30 | 1137 |  |  | 1421.25 |  | 1137.3805 |  | 3412141.6332 | 3412141.6331 |  | 1421.7257
4 | 13648566.533 | [11 empty] | 1137.3805
3 | 10236424.899 | [11 empty] | 853.0354
2 | 6824283.2663 | [11 empty] | 568.6903
1 | 3412141.6331 | [11 empty] | 284.3451
0.5 | 1706070.8166 | [11 empty] | 142.1726
0
[13 empty] | DT10 | DT30
[12 empty] | 1MW | 675 | 225
[12 empty] | 2MW | 1350 | 450
[12 empty] | 3 | 2000 | 700
[12 empty] | 4 | 2700 | 900
| Enter IT Power |  | 4 | [8 empty] | 5 | 3300 | 1150
| Enter T1 (to IT) |  | 80.6
| Enter Flow for IT |  | 2700 |  | Typcial range is 650 gpm to 2000 gpm
| Enter Target HRE |  | 0.9
| Enter HX Approach |  | 5
| Enter Flow for Heat |  | 600 |  | Typcial range is 650 gpm to 2000 gpm
| This is T2 (FROM IT) |  | 90.71
| This is T3 (to Heat) |  | 85.71
| This is T4 (from Heat) |  | 44.7643
| dt for IT |  | 10.11
| dt for Heat |  | 40.9457
Typical Range is 230 gpm to 750 gpm
Typcial range is 650 gpm to 2000 gpm

## Sample of Map Data (hidden)
Sample of Information as Taken From OCP "Heat Reuse Projects" Map | https://www.google.com/maps/d/u/0/viewer?hl=en&hl=en&ll=28.871726229013845%2C-40.21607810348212&z=3&mid=1bTp4Ugy7FGwfPadNlmfZpYwGY5Z5B7o
Date | 2023-03-01
Location | Golden CO, USA
Installed power | 2-5MW
Typical data center power | 2-3MW
Temperatures?
Typical temperature to IT equipment (°C) | 15-20C
Typical temperature from IT equipment (°C) | 30-35C
How is heat reused?
Within the building | Yes
Within the Campus | No
Off premises
If off prem distance of the heat host (in meters)
Elevating temperatures? (i.e. heat pump)
Primary Metric used?
Energy Reuse Effectiveness (ERE) | 0.9-0.95
Energy Reuse Factor (ERF)
Percentage of heat reused
Breakdown IT Cooling (in %)?
Air Cooled | 5-10%
Door Heat Exchanger | 5-10%
Cold Plate | 80-90%
Immersion
When did heat reuse start?
Business structure? | Self Use
Additional Info | https://drive.google.com/file/d/1W6hG85K4Oc6wiIk-MxPiFbGH9Q5tVp2N/view?usp=sharing
AZ115
AK148

## INSTALLED SYSTEMS DATABASE
[61 empty] | Construction Costs | [12 empty] | Operating Costs
Index | Data Source | Site Name | Date of given data | City of the site | Country of the site | Installed power of the site | Typical data center power (MW) | Typical temperature of cooling fluid to the IT equipment (Min) (°C) | Typical temperature of cooling fluid to the IT equipment (Max) (°C) | Typical temperature of cooling fluid from the IT equipment (Min) (°C) | Typical temperature of cooling fluid from the IT equipment (Max (°C) | Typical temperature of fluid To the Heat User (Min) (°C) | Typical temperature of fluid To the Heat User (Max) (°C) | Is the Heat User Within the building? | Is the Heat User Within the Campus? | Is the Heat User Off premises? | distance to the heat host (in meters) | Is extra equipment required to Elevate temperatures? (i.e. heat pump) | Heat Pump COP | Energy Reuse Effectiveness (ERE) | Energy Reuse Factor (ERF) | Percentage of heat reused | Amount of Heat Reused | How Much of the IT Equipment Air Cooled? | How Much of the IT Equipment use Door Heat Exchanger? | Does the IT Equipment have a Cold Plate? | IS the IT equipment cooled by Immersion? | When did heat reuse start? | What is the Business structure? | Type of User | Website Link | Other Links | Is there a product? | What was the cost of the IT facility or data center? | What was the cost to implement Heat Reuse? | How much power is used in the IT Facility or Data Center? | Data Center Space Size (m2) | Data Center Racks Size | Carbon Benefits | Other Benefits | Power/Energy Type |  | Fluid used in the IT Cooling Circuit | GWP of IT Cooling Fluid | ODP of IT Coolnig Fluid | Fluid Viscosity in IT Cooling Circuit | Temperature returning to the IT equipment | Fluid pressure entering the Heat Exchnager on the IT Cooling Side | Fluid Pressure leaving the heat exchanger on the IT Cooling Side | Fluid Flow in the IT Cooling Circuit | Fluid used in the Heat User Circuit | Fluid Viscosity in Heat User Circuit | Heat Capacity of Heat User Fluid | Temperature supplied To The Heat User | Temperature returning from the Heat User | Fluid pressure entiering the Heat Exchnager on the Heat User Side | Fluid Pressure leaving the heat exchanger on the Heat User Side | Fluid Flow in the Heat User Circuit | IS there SHORT TERM thermal storage of the heated fluid? | IS there LONG TERM thermal storage of the heated fluid? | Piping Diameter (IT Side) | Piping Length (IT Side) | Piping Insulation (IT Side) | Piping Diameter (Heat User Side) | Piping Length (Heat User Side) | Piping Insulation (Heat User Side) | Cost of Piping | Cost of Equipment | Ancillary IT Facility Costs | Ancillary Heat User Equipment Costs | Costs of Storage Equipment | Costs of Planning | Costs of Engineering | Water Usage | Water cost rate | Cost of Electricity
1 | Map+B2H | NREL | 2023-03-01 | Golden | Colorado | 2-5MW | 10 | 24 | 24 | 30 | 40 |  |  | Yes | No | No |  | No |  | 0.9-0.95 |  |  |  | 5-10% | 5-10% | 80-90% |  |  | Self Use | Laboratory | https://www.nrel.gov/computational-science/hpc-user-facility.html | https://drive.google.com/file/d/1W6hG85K4Oc6wiIk-MxPiFbGH9Q5tVp2N/view |  |  |  |  | 900
2 | B2H | Notre Dame |  | South Bend | Indiana | [24 empty] | Greenhouse | [7 empty] | 1
3 | B2H | Westin Building Exchange |  | Seattle | Washington | 5 MW | [23 empty] | Buildings | [8 empty] | 32 tons saved per year
4 | B2H | White Data Center Project | 1905-07-13 | Bibai | Japan |  | 40 | 33 | 33 |  |  | 27 |  | No | No | Yes | Adjacent | [15 empty] | 300,000 eels (75,000 kg)
5 | Map+B2H | Deep Green | 2023-05-10 | Exmouth | Great Britain | >1 MW | 28 | 40 | 44 | 50 | 54 | 30 |  | Yes | Yes | No | 0 | No |  |  |  | 96% |  | 0% | 0% | 0% | Yes |  | Heat provided for free |  | https://www.deepgreen.energy/ | We deploy data furnace tetology into sites which require hot water, to provide vital compute infrastructure – whilst providing significant additional, quantifiable ESG benefits. In exchange for hosting our kit and connectivity, we install free digital boilers alongside existing heating systems (and pay for the energy they use).
6 | Map+B2H | Ericsson | 2023-05-10 | Rosersberg | Sweden | 10 MW | 10 | 11 | 11 | 50 | 54 |  |  | Yes | No | No |  | No |  |  |  | >90% | 10 MW |  |  |  | Yes |  | Heat provided for free | District Heating | https://www.ericsson.com/en
7 | Map | atNorth | 2023-05-10 | Kista, Sweden | Sweden | >1 MW | >1 | 40 | 44 | 50 | 54 |  |  | Yes | No | No |  | No |  |  |  | >90% |  |  |  |  | Yes |  | Heat provided for free
8 | Map+B2H | Banhof | 2023-05-10 | Thule | Sweden | 1.6 MW | 1.2 | 40 | 44 | 50 | 54 | 65 | 100 | No | No | Yes |  | Heat Pumps |  |  |  | >90% |  |  |  |  | Yes |  | Heat provided for free | [5 empty] | SEK 8,900,000
9 | B2H | Banhof |  | Pionen | Sweden |  | 0.975 |  |  |  |  | 68 |  | No | No | Yes |  | Heat Pumps |  |  |  |  | 600 kW | 100% |  |  | No |  | Weather Dependent | District Heating |  |  |  | SEK 4,700,000
10 | B2H | Data Center Digiplex |  | Stockholm | Sweden |  | 5 | [15 empty] | 5 MW | 100% | [5 empty] | District Heating
11 | B2H | Container Data Center |  | Jordbro | Sweden | .55 MW | 0.55 | 50 | 50 |  |  | 60 |  | No | No | Yes |  | No | [11 empty] | District Heating
12 | B2H | Data Center H&M |  | Stockholm | Sweden | 1 MW | 1 | 6 | 6 | [8 empty] | Heat Pumps
13 | B2H | Datentechnik Moll |  | Boden | Sweden | 4.4 MW | 4.4 | [7 empty] | Yes | No | [10 empty] | Yes |  |  | Agriculture
14 | B2H | EcoDataCenter |  | Falun | Sweden | 2 MW | 2 | [22 empty] | Buildings and Wood Drying
15 | B2H | Edge data Center |  | Luleå | Sweden |  |  |  |  | 50 | 50 | 50 | [14 empty] | Yes | [13 empty] | Biomass Fuel Cells
16 | B2H | Green Hub |  | Stockholm | Sweden | 40 MW | [23 empty] | District Heating
17 | B2H | STO6 |  | Stockholm | Sweden | [6 empty] | 65 | 80 |  |  |  |  | Heat Pumps | [11 empty] | District Heating
18 | B2H | Stockholm Data Park |  | Stockholm | Sweden | 10 MW | [5 empty] | 85 | [5 empty] | Heat Pumps | [11 empty] | District Heating
19 | Map+B2H | Meta |  | Odense | Denmark | 1-2MW | 1.9 | 20 | 24 | [8 empty] | Heat Pumps |  |  |  |  | 100,000 MWh/a | [6 empty] | District Heating
20 | Map+B2H | IBM Resaerch (GIB Services) | 2023-05-10 | Uitikon | Switzerland | <1 | 0.32 | 40 | 44 | 50 | 54 |  |  | Yes | No | No |  | No |  |  |  | >90% |  |  |  |  | Yes |  | Heat provided for free | Pool | https://www.zurich.ibm.com
21 | B2H | Data Center Eastern Switzerland |  | Gais | Switzerland |  | 1.5 | 14 | 14 | 20 | 20 | 100 |  | No | No | Yes | Adjacent | Heat Pumps | [11 empty] | Agricultural |  |  | 18,000,000 lliters of milk + some cheese |  |  |  | 200
22 | B2H | Eco-Qube |  | Dùindorf | Switzerland | [12 empty] | Heat Pumps
23 | Map | Smart DC |  | Rotterdam | Belgium | >1 MW | 10-19.9MW | 20 | 24 | 30 | 34 |  |  | No | Yes | Yes | 100 - 200 | Yes |  | 0.8-0.89 | 0.5-0.59 | 20-30% |  | 5-9% | 30-39% | 60-69%
24 | Map | NorthC |  | Rotterdam | Belgium | >1 MW | 10-19.9MW | 20 | 24 | 30 | 34 |  |  | No | Yes | Yes | 100 - 200 | Yes |  | 0.8-0.89 | 0.5-0.59 | 20-30% |  | 5-9% | 30-39% | 60-69%
25 | Map+B2H | LUMI Supercomputer | 2021 | Kajaani | Finland | 5-10MW | 5-9.9MW | [6 empty] | Yes | Yes | Yes | 100 - 200 | Heat Pumps |  |  |  | >90% |  | 5-9% | [6 empty] | https://www.lumi-supercomputer.eu |  |  | 202000000 |  |  |  |  | 13500 tons saved |  | Hydroelectricity
26 | Map | Hetzner Finland Oy | 2023-05-10 | Tusuula, FI | Finland | >1 MW | 1 | 40 | 44 | 50 | 54 |  |  | Yes | No | No |  | No |  |  |  | >90% |  |  |  |  | Yes |  | Heat provided for free |  | www.hetzner.com
27 | Map | Ficolo | 2023-06-13 | Vantaa | Finland | 5-10MW | 5-9.9MW | 20 | 24 | 35 | 39 |  |  |  |  | Yes | 200 - 500 | Yes |  |  |  | 20-30% |  | >90% |  |  |  | 2021 | Heat Sold |  | https://finland.verneglobal.com/en/data-centers/the-air/ | provided water temperature 95-100*C
28 | Map | Tietoevry Oyj | 2023-05-10 | Espoo, FI | Finland | >1 MW | 1 | 40 | 44 | 50 | 54 |  |  | Yes | No | No |  | No |  |  |  | >90% |  |  |  |  | Yes |  | Heat provided for free
29 | Map+B2H | Academica |  | Helsinki | Finland | 2 MW | 2 | 20 | 24 | 30 | 34 |  |  | No | Yes | Yes | 100 - 200 | Yes |  | 0.8-0.89 | 0.5-0.59 | 20-30% |  | 5-9% | 30-39% | 60-69% |  |  |  |  | https://www.future-tech.co.uk/treat-your-data-centre-as-an-energy-source/
30 | B2H | Data Center in Mäntsälä |  | Helsinki | Finland | [6 empty] | 85 |  | No | No | Yes | 200 | Heat Pumps
31 | B2H | Elisa HQ |  | Helsinki | Finland | [33 empty] | 250 tons saved
32 | B2H | Ericscsson Data Center |  | kirkonummi | Finland | [37 empty] | HFO-1234ze
33 | B2H | Nokia Data Center vLab | 2022 | Tampere | Finland | [6 empty] | 95 | [5 empty] | Heat Pumps
34 | B2H | Pitäjänmäki Dat Centre | 2022 | Helsinki | Finland |  | 24 | [10 empty] | Heat Pumps
35 | B2H | 3D Animation Studio | 2018 | Paris | France | >1 MW | 1 |  |  |  |  | 27 | [9 empty] | 100% |  | 0% | 0% | 0% | Yes |  |  | Swimming Pool | [8 empty] | 45 tons CO2 Saved
36 | B2H | Data Center Telecity |  | Paris | France | [8 empty] | Yes | Yes | No | [5 empty] | 100%% |  |  |  |  | No |  |  | Arboretum
37 | B2H | Q.Rad Heaters |  | Paris | France |  | 0.15 | [6 empty] | Yes | Yes | No | [5 empty] | 100%% | 150 kW | 100% |  |  | No |  |  | Building
38 | Map | Green Computing |  | Paris | France | 10-20MW | 10-19.9MW | 20 | 24 | 30 | 34 |  |  | No | Yes | Yes | 100 - 200 | Yes |  | 0.8-0.89 | 0.5-0.59 | 20-30% |  | 5-9% | 30-39% | 60-69% |  |  |  |  | https://greendata.fr
39 | Map | Leibniz-Rechenzentrum | 2023-05-10 | Munich | Germany | >1 MW | 1 | 40 | 44 | 50 | 54 |  |  | Yes | No | No |  | No |  |  |  | >90% |  |  |  |  | Yes |  | Heat provided for free |  | https://www.lrz.de
40 | Map+B2H | Volkwagen Financial | 2023-05-10 | Braunschweig | Germany | 0.25 | 0.25 |  |  |  |  | 70 |  | No | No | Yes | 3000 | No |  |  |  | >90% |  |  |  |  | Yes |  | Heat provided for free |  | 404 |  |  | 460000
41 | Map | Cloud & Heat |  | Frankfurt | Germany | 10-20MW | 10-19.9MW | 20 | 24 | 30 | 34 |  |  | No | Yes | Yes | 100 - 200 | Yes |  | 0.8-0.89 | 0.5-0.59 | 20-30% |  | 5-9% | 30-39% | 60-69%
42 | Map | Data Castle |  | Frankfurt | Germany | >1 MW | 10-19.9MW | 20 | 24 | 30 | 34 |  |  | No | Yes | Yes | 100 - 200 | Yes |  | 0.8-0.89 | 0.5-0.59 | 20-30% |  | 5-9% | 30-39% | 60-69%
43 | B2H | Algae Farm |  | Enge-Sande | Germany | 15 MW | 6 MW | [6 empty] | No | Yes | No | On Roof |  |  |  |  | 100% | 60 kW | [6 empty] | Agricultural |  |  | "Lüttge" nutritional supplements by Evergreen-Food GmbH | 550000 |  | 60 kW |  | 24 | 1 kg of algae consumes 2 kg of carbon |  | 98% Wind
44 | B2H | Campus Lichtwiese |  | Darmstadt | Germany |  |  |  |  | 60 | 60 | 70 | [21 empty] | 15000000
45 | B2H | Colocation Westend |  | Bremen | Germany |  | 0.8
46 | B2H | Data Center at Wallotstraße |  | Dresden | Germany | [6 empty] | 60 | [7 empty] | 0.62
47 | B2H | Data Center Cologne |  | Cologne | Germany | [25 empty] | There is no data
48 | B2H | Data Center Kelsterbach (Lufthansa) |  | Kelsterbach | Germany | [25 empty] | There is no data
49 | B2H | Green Cube |  | Darmstadt | Germany | [17 empty] | 12 MW | [10 empty] | 2800000
50 | B2H | Gym Heating |  | Hamburg | Germany | [31 empty] | 200 | 63
51 | B2H | Heinrich-Böll-Foundation |  | Berlin | Germany |  |  | 23 |  |  |  | 30 |  | Yes | No | No | 0
52 | B2H | Eurotheum |  | Frankfurt | Germany |  | 0.6 | [14 empty] | 90% | [7 empty] | Building | [8 empty] | 557 tons saved | Cooling savings of 95,000 Euros and heating savings of 65,000 Euros
53 | B2H | Horeka High Performance Computer |  | Karlruhe | Germany | [24 empty] | Building |  |  |  | 15000000
54 | B2H | Location |  | Hannover | Germany | 5 MW | [30 empty] | 4000
55 | B2H | LRZ |  | Munchen-Garching | Germany |  | 4 | 50 |  |  |  | 60 | [17 empty] | Building
56 | B2H | NTT Munich 2 |  | Munich | Germany | [8 empty] | Yes | Yes | No | [6 empty] | .34 MW | [6 empty] | Building |  |  |  | 12100000
57 | B2H | New Mecklenburg Building |  | Griefswald | Germany | [36 empty] | There is insuffient data
58 | B2H | University of Hamburg |  | Hamburg | Germany
59 | B2H | University of Stuttgart |  | Stuttgart | Germany |  | 3.5 | 25 |  | 35 |  | 70
60 | B2H | Unterfräkische Überlandzentrale |  | Lülsfeld | Germany |  |  | 22 |  |  |  | 35 | [5 empty] | Heat Pumps
61 | B2H | Züblin Z3 |  | Stuttgart | Germany | [8 empty] | Yes | No | No | [13 empty] | Building | [11 empty] | This is air-to-air
64 | B2H | Londoner Docklands | 2010 | London | Great Britain | [17 empty] | 9 MW | [6 empty] | Buildings | [8 empty] | 1100 Tons saved
65 | B2H | Data Center Digiplex |  | Kopenhagen | Denmark | [24 empty] | District Heating
66 | B2H | Data Center Viborg |  | Viborg | Denmark | [24 empty] | District Heating
67 | B2H | Supercomputer Center DTU |  | Risø | Denmark | [12 empty] | Heat Pumps |  |  |  |  | 600 kW | [6 empty] | District Heating | [6 empty] | 3800
68 | B2H | Blockheating |  | Venlo | Netherlands |  | 0.2 |  |  |  |  | 65 | [17 empty] | Agriculture | Implements used IT gear
69 | B2H | Equinix AM3 |  | Amsterdam | Netherlands | 14 |  |  |  | 20 |  | 30 | [9 empty] | 80%
71 | B2H | DC1-Stavenger |  | Rennesøy | Norway |  | 52 |  |  | 8 |  | 20 |  | No | No | Yes | Adjacent | No |  |  |  |  | 52 MW | [6 empty] | Lobster Farm |  |  | 900 tons of Lobster |  |  |  | 22600 | [13 empty] | Sea water
72 | B2H | DC2-Telemark |  | Rjukan | Norway | 20 MW | [10 empty] | 800 | [5 empty] | 20 MW | [6 empty] | Trout Farm |  |  | 9000 tons of trout | 100000000
73 | B2H | Ulven |  | Oslo | Norway |  | 3.5 | [15 empty] | 3.5 MW
IN PLANNING / IMPLEMENTATION
74 | B2H | Data Center Val d Europe |  | Val d Europe | France |  | 7.8 |  |  |  |  | 55 |  |  |  |  | 4 | Boilers |  |  |  | 100% | 7.8 MW | [6 empty] | Buildings |  |  |  | 3500000 |  |  |  |  | 4,000 tons saved
75 | B2H | Data Center PA10 |  | Paris | France | [24 empty] | Pool + Greenhouse |  |  |  | 163000000 |  |  | 3775 | 1525
76 | B2H | London Data Freeport |  | Havering | Great Britain |  | 0.6 | [22 empty] | Agriculture |  |  |  | 5300000000 |  |  | 330000
77 | B2H | AWS Data Center |  | Dublin | Ireland | [24 empty] | Buildings | [8 empty] | 1500 tons saved
78 | B2H | Ecologic |  | Newtown Mount Kennedy | Ireland |  | 0.15 | [15 empty] | 150 MW | [6 empty] | Biodomes | [8 empty] | Carbon Neutral
79 | B2H | Data Center Danfoss |  | Nordborg | Denmark | 1 MW | 1 | [6 empty] | Yes | Yes | No | [13 empty] | General Heating
80 | B2H | Equinix HE3 & HE5 |  | Helsinki | Finland | [24 empty] | District Heating
81 | B2H | Microsoft Data Center |  | Espoo | Finland | [24 empty] | District Heating | [8 empty] | 400000 tons saved
82 | B2H | Data Castle 25 MVA Data Center |  | Schwalbach am Taunus | Germany | 25 MVA | [34 empty] | Solar Panels
83 | B2H | Audi In Campus |  | Ingolstadt | Germany |  | 2 | 22 |  | 30 |  | 45 |  |  |  |  | 3000 | Heat Pumps |  |  |  |  | 2MW | [6 empty] | District Heating | [28 empty] | Subterranean Storage
84 | B2H | Data Center Heated Night Club |  | Frankfurt Seckbach | Germany |  | 30 | [9 empty] | 500 | Heat Pumps | [11 empty] | Building | [6 empty] | 10500
85 | B2H | Equinix FR4, FR6 & FR8 |  | Frankfurt Griesheim | Germany |  | 56 | [9 empty] | 2000 |  |  |  |  | 70% | [7 empty] | District Heating
86 | B2H | Franky |  | Frankfurt Gallus | Germany | 20 | 14 |  |  | 30 |  | 70 |  |  |  |  | 260 | Heat Pumps
87 | B2H | JH Computers |  | Stödtlen | Germany |  | 1 | [9 empty] | Adjacent | Heat Pumps | [18 empty] | 220 | 50
88 | B2H | Equinix MU4 |  | Munich | Germany | [24 empty] | District Heating |  |  |  | 90000000 |  |  | 2250 | 825
89 | B2H | nLighten data Center |  | Eschborn | Germany |  | 2.4 | [9 empty] | 800
90 | B2H | NTT Voltastraße |  | Hattersheim | Germany
91 | B2H | ZIH TU Dresden |  | Dresden | Germany | [12 empty] | Heat Pumps | [15 empty] | 1600000
92 | B2H | Stack 80 MW data Center |  | Taunus | Germany |  | 80 | [29 empty] | 70000
93 | B2H | Data Center at ICE Train Station |  | Limburg | Germany |  | 35 |  |  |  |  | 30 | [21 empty] | 100000000 |  |  | 10330
94 | B2H | Digital Park |  | Frankfurt Fechenheim | Germany |  | 20 | [10 empty] | Heat Pumps
95 | B2H | heiCOMACS |  | Heidelberg | Germany |  | 54 | [10 empty] | Heat Pumps |  |  |  |  | 60 | [10 empty] | 15000000
96 | B2H | Ingelheimer Aue |  | Ingelheimer Aue | Germany
97 | B2H | Jupiter Project |  | Jülich | Germany |  | 15 | [26 empty] | 500000000
98 | B2H | Evo (An den Eichen) |  | Offenbach | Germany |  | 9 | [15 empty] | 9
99 | Map+B2H | Interxion | 2023-05-10 | Kista, Sweden | Sweden | >1 MW | 1 | 14 |  |  |  | 24 |  |  | No | No |  | Heat Pumps |  |  |  | >90% |  |  |  |  | Yes |  | Heat provided for free |  | https://www.ericsson.com/en | [5 empty] | 4800
100 | B2H | Elementica |  | Stockholm | Sweden |  | 21 | [8 empty] | Yes | 250 | [5 empty] | 10 MW | [5 empty] | Sold to Biomass | Biomass Processing |  | See notes regading tax implications
101 | B2H | EcoDataCenter2 |  | Östersund | Sweden |  | 20 | [15 empty] | 20 MW | [6 empty] | Fish Farm + Food Production
102 | B2H | Qscale Q01 Campus |  | Quebec | Canada |  | 96 | [25 empty] | 2,800 Tons of berries + 80,000 tons tomatoes
103 | B2H | Aalsmeer Energy Hub |  | Aalsmeer | Netherlands |  | 4 | 12 |  | 25 |  | 22 | [17 empty] | Agricultural
104 | B2H | Data Center Bytesnet |  | Groningen | Netherlands |  | 0.2 | [19 empty] | Yes
105 | B2H | Interxion AMS5 |  | Schipol-Rijk | Netherlands | [24 empty] | Industrial Dictrict
106 | B2H | Switch Datacenters |  | Woerden | Netherlands |  |  |  |  | 60
107 | B2H | QTS Datacenter |  | Groningen | Netherlands | [16 empty] | 100%
108 | B2H | Airport City Energy Network |  | Zurich | Switzerland | [24 empty] | Industrial Dictrict
109 | Map+B2H | Wyoming Hyperscale |  | Evanston | Wyoming |  | 120 | [14 empty] | 100% | [7 empty] | Agricultural |  |  | food
110
111
HJ600

## Data DICTIONARY R12
password | SEE COLUMN "N" TO OFFER FEEDBACK OR COMMENTS
| Data Point Name | Data Point Description | Variable Name | Data Type | Units | DATA Table Column Location | VISUALIZATION Template Column Location | Default | Anticipated Range of Values | Source of Input Data | THE CELLS IN COLUMN "N" ARE OPEN FOR LINE-BY-LINE COMMENTS AND FEEDBACK You can also add columns and/or rows,
INTRODUCTORY INFORMATION | Index | Identifier for each unique Record | index | int |  | A | A | n+1 | 1 - 5000 | Engine
| Data Source | Source that the data was gathered from | source | string | n/a | D | B | Client | 30 char | Engine
| Party Inputting the Data, per Record | Regardless of existing or new record, the common name for "where did it come from" | Client | string | n/a | C |  | Client | 30 char | Client
| Site Name | The "Common" name for the site | name | string | n/a | B | C | n/a | 50 char | Client
| Date of given data | Date of entry of the data | date1 | Date | 2023-12-31 | E | D | 2023-12-31 | date | Client
| Date of latest update | Date of last update of the data | date2 | Date | 2023-12-31 | F |  | 2023-12-31 | date | Client
| City of the site | Nearest City to the site location | city | string | n/a | G | E | n/a | 30 char | Client
| State | State or region of the site location | state | string | n/a | H |  | n/a | 30 char | Client
| Country of the site | Country of the location | country | string | n/a | I | F | n/a | 30 char | Client
| IT Facility Latitude | Geographical Latitude of the site | sitelat | float | decimal degrees | J |  | n/a | -80.000000 to 80.000000 | Client
| IT Facility Longitude | Geographical Longitude of the site | sitelong | float | decimal degrees | K |  | n/a | -180.000000 to 180.000000 | Client
| IT Facility Elevation | Height above Mean Sea Level | siteelv | float | meters | KU |  | 100 | -100 to 5000 | Client
| Heat Offtaker Latitude | Geographical Latitude of the heat Offtaker | oftkrlat | float | decimal degrees | L |  | n/a | -80.000000 to 80.000000 | Client
| Heat Offtaker Longitude | Geographical Longitude of the heat Offtaker | oftkrlong | float | decimal degrees | M |  | n/a | -180.000000 to 180.000000 | Client
| Heat Offtaker Elevation | Height above Mean Sea Level | oftkrelv | float | meters | KU |  | 100 | -100 to 5000 | Client
| Site Owner | Principal owner of the Data Facility | siteowner | string | n/a | N |  | n/a | 100 char | Client
| Site Owner Website or Links | Any online information regarding site owners | soweblink | hyperlink | n/a | O | AF | n/a | url | Client
| Data Centre Principal Tenant or User | Principal tenant or user of the site | ituser | string | n/a | P |  | = siteowner | 100 char | Client
| Data Centre Space Size (m2) | Footprint area of the white space | warea | float | square meters | Q | AL | n/a | 100 to 9999 | Client
| Data Centre Racks Size | The number of data cabinets of racks | rack | int | count | R | AM | n/a | 1 to 100000 | Client
| IT Power Per Rack | The avaerage amount of power per standard rack | rackkw | float | kiloWatts | S |  | n/a | 1 to 300 | Client
| Tenant Website or Links | Any online information regarding tenants or users of the data centre | itweblink | hyperlink | n/a | T | AG | n/a | url | Client
| Heat Offtaker System Owner | Principal owner of the Heat Offtaker System | oftkrowner | string | n/a | U |  | n/a | 100 char | Client
| Heat Offtaker Owner Website or Links | Any online information regarding the owner/operator of the heat Offtaker system | howeblink | hyperlink | n/a | V | AO | n/a | url | Client
| Heat Offtaker Principal Offtaker | Principal Offtaker of the heat | oftkruser | string | n/a | W |  | =huowner | 100 char | Client
| Heat Offtaker Website or Links | Any online information regarding the actual Offtaker(s) of the heat | huweblink | hyperlink | n/a | X | AP | n/a | url | Client
| Type of Offtaker | General category of heat Offtaker | oftkrtype | string | n/a | Y | AE | SELECTION BOX: Agricultural, Biomass Processing, Building HVAC Reheat, Decarbonization, District Energy, Ethanol Production, Fish Farming – Freshwater, Fish Farming. – Seawater, Greenhouse, Heat Storage in Aquafer, Hospital, Hotel, Industrial Laundry, Private District Energy, Swimming Pool, Wastewater Treatment | 30 char. Box | Client
| What is the Business structure? | Short explanation of the relationship between the It Facility and the Heat Offtaker | relationship | string | n/a | Z | AD | n/a | 250 char | Client
| When did heat reuse start? |  | date3 | Date | 2023-12-31 | AA | AC | 2023-12-31 | date | Client
| Is there a product resulting from the heat reuse? | What does the Heat Offtaker get from the use of the heat, if there is an "industrial" Offtaker? | product | string | n/a | AB | AH | No | 250 char | Client
| Data Centre Throughput | What is the size of the computing equipment, in "Computing Terms" | datasize | float | pflops | DA |  | n/a |  | Client
DATA HALL STUFF | Amount Cooled by Air ("traditional") (%) | How much of the IT Equipment is Cooled by Air ("traditional") (%) | itaircl | float | % | DB | Y | n/a | <1.0 | Client
| Amount Cooled by Rack Door Heat Exchanger (%) | How much of the IT Equipment is Cooled by Rack Door Heat Exchanger (%) | itdrcl | float | % | DC | Z | n/a | <1.0 | Client
| Amount Cooled by "Direct-to-Chip" Cold Plate (%) | How much of the IT Equipment is Cooled by "Direct-to-Chip" Cold Plate (%) | itchipcl | float | % | DD | AA | n/a | <1.0 | Client
| Amount Cooled by "Other" Cold Plate (%) | How much of the IT Equipment is Cooled by "Other" Cold Plate (%) | itpltcl | float | % | DE |  | n/a | <1.0 | Client
| Amount Cooled by Single Phase Immersion (%) | How much of the IT Equipment is Cooled by Single Phase Immersion (%) | it1imm | float | % | DF | AB | n/a | <1.0 | Client
| Amount Cooled by Two Phase Immersion (%) | How much of the IT Equipment is Cooled by Two Phase Immersion (%) | it2imm | float | % | DG | AB | n/a | <1.0 | Client
| Data Centre Load Daily Fluctuation | Daily swing in available heat, from Client input | itdivrday | float | % | DH |  | 1 | (calculated) | Engine
| Data Centre Load Annual Fluctuation | Annual swing in available heat, from Client input | itdvryr | float | % | DI |  | 1 | (calculated) | Engine
| Waste Heat Available, Adjusted for Fluctuation | Total Waste Heat Available, multiplied by both Fluctuation factors | whadvr | float | % | DJ |  | =wha | (calculated) | Client
| RESERVED |  | n |  |  | DK |  |  |  | Client
| RESERVED |  | n |  |  | DL |  |  |  | Client
ENERGY INFORMATION | Installed power of the site | Installed power of the site | sitepwr | float | MegaWatts | AC | G | n/a | 0.0 - 500.0 | Client
| Rated data Centre power | Rated data Centre power | itpwr | float | MegaWatts | AD | H | n/a | 0.0 - 500.0 | Client
| Primary Electrical Power Source | Primary Electrical Power Source | pwrsce1 | string | n/a | AE |  | n/a | 50 char | Client
| Primary Source Type | Primary Source Type | pwrtype1 | string | n/a | AF | AP | n/a | 50 char | Client
| Base Cost Rate for Primary Power | Base Cost Rate for Primary Power | pwrrate1 | float | FORMAT?? | AG |  | n/a |  | Client
| Rate Adjustments to Power Base Rate | Rate Adjustments to Power Base Rate | pwrrate1ad | float | n/a | AH |  | n/a |  | Client
| Proportion of Total Power From Primary Source | Proportion of Total Power From Primary Source | pwr1prop | float | n/a | AI |  | 1 | 0 - 1.0 | Client
| Secondary Power Source | Secondary Power Source | pwrsce2 | string | n/a | AJ |  | n/a | 50 char | Client
| Secondary Source Type | Secondary Source Type | pwrtype2 | string | n/a | AK |  | n/a | 50 char | Client
| Base Cost Rate for Secondary Power | Base Cost Rate for Secondary Power | pwrrate2 | float | FORMAT?? | AL |  | n/a |  | Client
| Rate Adjustments to Secondary Power Base Rate | Rate Adjustments to Secondary Power Base Rate | pwrrate2ad | float | FORMAT?? | AM |  | n/a |  | Client
| Proportion of Total Power From Secondary Source | Proportion of Total Power From Secondary Source | pwrrate2prop | string | n/a | AN |  | n/a |  | Client
| Alternate or Additional Fuels | Alternate or Additional Fuels | pwralt | string | n/a | AO |  | n/a |  | Client
| Alternalte Fuel Type | Alternalte Fuel Type | pwralttype | string | n/a | AP |  | n/a |  | Client
| Base Cost rate for Alternate or Additional Fuels | Base Cost rate for Alternate or Additional Fuels | pwrratealt | float | n/a | AQ |  | n/a |  | Client
| Rate Adjustments to Alternate Fuels Base Cost Rate | Rate Adjustments to Alternate Fuels Base Cost Rate | pwrratealtad | float | n/a | AR |  | n/a |  | Client
| Water Usage | Water Usage | h2ouse | float | liters per year | AS | CR | 0 |  | Client
| Water cost rate | Water cost rate | h2orate | float | FORMAT?? | AT | CS | 0 |  | Client
| Is the Heat Offtaker Within the building? | Is the Heat Offtaker Within the building? | oftkrbldg | string | Yes / No | AU | O | No | Yes / No | Client
| Is the Heat Offtaker Within the Campus? | Is the Heat Offtaker Within the Campus? | oftkrcamp | string | Yes / No | AV | P | Yes | Yes / No | Client
| Is the Heat Offtaker Off premises? | Is the Heat Offtaker Off premises? | oftkrprem | string | Yes / No | AW | Q | Yes | Yes / No | Client
| Distance to the Heat Offtaker | When Offtaker is off-premises, how far to the first Offtaker | oftkrdist | int | meters | AX | R | 0 | 0 to 5000 | Client
| Energy Reuse Effectiveness (ERE) | Use these figures if offered by Client | ere | float | none | AY | U | 0.8 | 0 <1.0 | Client
| Energy Reuse Factor (ERF) | Use these figures if offered by Client | erf | float | none | AZ | V | 0.8 | 0 <1.0 | Client
| Heat Reuse Effectiveness (HRE) | Use these figures if calculated within our engine | hre | float | none | BA |  | (calculated) | 0 <1.0 | Engine
| Heat Reuse Factor (HRF) | Use these figures if calculated within our engine | hrf | float | none | BB |  | (calculated) | 0 <1.0 | Engine
| Percentage of Heat Reused | Use these figures if offered by Client | hrec | float | % | BC | W | 80% | 0 <1.0 | Client
| Amount of Heat Reused | Use these figures if offered by Client | hrfc | float | MW | BD | X |  | 0 <1.0 | Client
| Total Heat Available | Heat made available from the IT System | wha | float | MW | BE |  | (calculated) | 0.0 to 5000.0 | Engine
| Total Heat Reused | Heat actually processed by Offtaker system | uhr | float | MW | BF |  | (calculated) | 0.0 to 5000.0 | Engine
| Total Heat Reused, Adjusted for Fluctuation | Total Heat multiplied by both Fluctuation factors | uhrdvrad | float | MW | BG |  | (calculated) | 0.0 to 5000.0 | Engine
| HRE, Adjusted for Fluctuation | Hre, adjusted by all four factors | hredvrad | float | MW | BH |  | (calculated) | 0.0 to 5000.0 | Engine
MECHANICAL OPERATING PARAMETERS | Electrical Power to operate IT Medium stream | Mostly, will be the pump power | pwrf1 | float | kW | BI |  | 25 | 1.0 - 500.0 | Client
| Temperature to the IT equipment (Min) | Temperature to the IT equipment (Min) | T1min | float | Degrees (C) | BJ | I | 10 | 10.0 - 40.0 | Client
| Temperature to the IT equipment (Max) | Temperature to the IT equipment (Max) | T1max | float | Degrees (C) | BK | J | 40 | 10.0 - 40.0 | Client
| Rated temperature to the IT equipment | Rated temperature to the IT equipment | T1 | float | Degrees (C) | BL | BG | 30 | 10.0 - 40.0 | Client
| Ttemperature from the IT equipment (Min) | Ttemperature from the IT equipment (Min) | T2min | float | Degrees (C) | BM | K | 20 | 10.0 - 70.0 | Client
| Temperature from the IT equipment (Max) | Temperature from the IT equipment (Max) | T2max | float | Degrees (C) | BN | L | 60 | 10.0 - 70.0 | Client
| Rated temperature from the IT equipment | Rated temperature from the IT equipment | T2 | float | Degrees (C) | BO |  | 40 | 10.0 - 70.0 | Client
| Temperature difference across IT side of heat exchanger | Temperature difference across IT side of heat exchanger | itdt | float | Degrees (C) | BP |  | (calculated) | 10.0 - 70.0 | Engine
| Medium used in the IT Cooling Circuit | What is the medium being used for capturing heat from the IT system? | fluid1 | string | n/a | BQ | AR | Water |  | Client
| Pressure entering IT Cooling Side | Gauge Pressure of the Cooling Medium at the Heat Exchanger | P2 | float | bar | BR | AW | 4.0 | 1.0 - 25.0 | Client
| Pressure leaving IT Cooling Side | Gauge Pressure at the Cooling Medium as delivered from the Heat Exchanger | P1 | float | bar | BS | AX | 1.0 | 1.0 - 25.0 | Client
| Pressure drop on IT side | Heat Exchanger "Delta P", on the IT Side | dpit | float | bar | BT |  | (calculated) |  | Engine
| Medium Flow in the IT Cooling Circuit | Fluid flow of IT Cooling Medium | F1 | float | Liters per Minute | BU | AY |  | 250 - 10000 | Client
| Fluid Viscosity in IT Cooling Circuit | Viscosity of IT Cooing Medium | fluid1vis | float | n/a | BV | AU | n/a |  | Client
| Heat Capacity of IT Cooling Medium | Heat Capacity of IT Cooling Medium | fluid1hc | float | n/a | BW |  | n/a |  | Client
| Material for the Piping in the IT Cooling Circuit | Materials for the majority of the piping in the cooling circuit | Itpipe | string | n/a | HY |  | steel | Steel, Grooved Steel, Plastic, Copper, Stainless, Grooved Stainless | Client
| GWP of IT Cooling Medium | GWP of IT Cooling Medium | gwp1 | float | n/a | BX | AS | n/a |  | Client
| ODP of IT Cooling Medium | ODP of IT Cooling Medium | odp1 | float | n/a | BY | AT | n/a |  | Client
| Typical temperature of Medium returning from the Heat Offtaker (Min) | Typical temperature of Medium returning from the Heat Offtaker (Min) | T4min | float | Degrees (C) | BZ |  | 20 | 10.0 - 40.0 | Client
| Typical temperature of Medium returning from the Heat Offtaker (Min) | Typical temperature of Medium returning from the Heat Offtaker (Min) | T4min | float | Degrees (C) | BZ |  | 20 | 10.0 - 40.0 | Client
| Typical temperature of Medium returning from the Heat Offtaker (Max) | Typical temperature of Medium returning from the Heat Offtaker (Max) | T4max | float | Degrees (C) | CA |  | 40 | 10.0 - 50.0 | Client
| Rated temperature of Medium FROM the Heat Offtaker | Rated temperature of Medium FROM the Heat Offtaker | T4 | float | Degrees (C) | CB |  | 25 | 10.0 - 50.0 | Client
| Typical temperature of Medium To the Heat Offtaker (Min) | Typical temperature of Medium To the Heat Offtaker (Min) | T3min | float | Degrees (C) | CC | M | 30 | 10.0 - 60.0 | Client
| Typical temperature of Medium To the Heat Offtaker (Max) | Typical temperature of Medium To the Heat Offtaker (Max) | T3max | float | Degrees (C) | CD | N | 50 | 10.0 - 60.0 | Client
| Rated temperature of Medium TO the Heat Offtaker | Rated temperature of Medium TO the Heat Offtaker | T3 | float | Degrees (C) | CE |  | 45 | 10.0 - 60.0 | Client
| Temperature Difference across Offtaker side of heat exchanger | Temperature Difference across Offtaker side of heat exchanger | oftkrdt | float | Degrees (C) | CF |  | (calculated) | 10.0 - 70.0 | Engine
| Material for the Piping for the Heat Offtaker Circuit: | Material for the Piping for the Heat Offtaker Circuit: | oftkrpipe | string | n/a | HZ |  | steel | Steel, Grooved Steel, Plastic, Copper, Stainless, Grooved Stainless | Client
| Medium used in the Heat Offtaker Circuit | What is the medium being used for heating? | fluid2 | string | n/a | CG | BE | Water | 50 char | Client
| Medium pressure entering the heat exchnager on the Heat Offtaker Side | Gauge Pressure at the Heat Exchanger | P4 | float | bar | CH |  | 5 | 1.0 - 25.0 | Client
| Medium Pressure leaving the heat exchanger on the Heat Offtaker Side | Gauge Pressure at the Heat Exchanger | P3 | float | bar | CI |  | 3 | 1.0 - 25.0 | Client
| Medium Pressure drop across heat exchanger on Offtaker side | Heat Exchanger "Delta P", on the Offtaker Side | oftkrdp | float | bar | CS |  | (calculated) |  | Engine
| Medium Flow in the Heat Offtaker Circuit | What is the fluid flow in the Offtaker side? | F2 | float | Liters per Minute | CJ | BL |  |  | Client
| Fluid Viscosity in Heat Offtaker Circuit | What is the viscosity of the Medium on the Offtaker side? | fluid2vis | float |  | CL | BF |  |  | Client
| Heat Capacity of Heat Offtaker Medium | What is the Heat Capacity of the Offtaker side Medium? | fluid2hc | float |  | CM | BG |  |  | Client
| Is there SHORT TERM thermal storage of the heated Medium? | If there is some kind of buffer tank? | storst | string | Yes / No | CN | BM | No | Yes / No | Client
| Size of the short term storage | How much Medium is stored or buffered? | storstsz | float |  | CO |  |  |  | Client
| Type of Short Term Storage | What type of storage is there? | storsttyp | string | n/a | CP |  | Tank | 50 char | Client
| Is there LONG TERM thermal storage of the heated Medium? | If there is a reservior or large body of water? | storlt | string | Yes / No | CQ | BN | No | Yes / No | Client
| Size of the long term storage | What is the volume of the large, long term storage? | storltsz | float |  | CR |  |  |  | Client
| Type of Long Term Storage | What type of storage is there? | storlttyp | string | n/a | CT |  | Reservior | 50 char | Client
| Is extra equipment required to Elevate temperatures? | If the Offtaker side Medium is not suffiently warm enough for the Offtaker's benefit, how is it further heated? | boost | string | Yes / No | CK | AB | No | Yes / No | Client
| What Equipment Type? | What is used to boost the temperature to make it "usable"? | boosteqp | string | n/a | CU |  | Heat Pump | "Heat Pump", "Boiler" | Client
| Heat Pump COP | IF a heat pump is used, how efficient is that heat pump? | bsthpcop | float | n/a | CV | AC |  | 0.5 - 1.0 | Client
| Boiler Efficiency | IF a boiler is used, how efficient is that boiler? | bstblreff | float | n/a | CW |  |  | 0.5 - 1.0 | Client
| Electrical Power to operate Offtaker Medium stream | Power for fluid movement on the Heat Offtaker side | pwrf2 | float | kW | CX |  | 25 | 1.0 - 1000.0 | Client
| Offtaker Daily Fluctuation Factor | Calculated from Client Input, DAILY swing in Usage | dvrusrday | float | n/a | CY |  | 1 | (calculated) | Engine
| Offtaker Seasonal Fluctuation Factor | Calculated from Client Input, ANNUAL swing in Usage | dvrusryr | float | n/a | CZ |  | 1 | (calculated) | Engine
Offtaker BUSINESS COSTS/BENEFITS | Offtaker Industrial Product 1 | Is there an industrial use for the heat? If so, what is the primary product? | prod1 | string |  | DM | AH | No | 100 char | Client
| Offtaker Product 1 Annual Revenue | Annual revenue to Offtaker from Product 1 | prod1rev | float | € | DN |  | 0 | 0 | Client
| Offtaker Industrial Product 2 | Is there an industrial use for the heat? If so, what is the secondary product? | prod2 | string |  | DO |  | No | 100 char | Client
| Offtaker Product 2 Annual Revenue | Annual revenue to Offtaker from Product 2 | prod2rev | float | € | DP |  | 0 | 0 | Client
| Offtaker Cost of Alternative Heat | What would heat cost RATE if there were no reuse? | althtrate | float | € | DQ |  |  |  | Client
| Cost of electricity (Offtaker) |  | usrpwrrate | float | € | DR |  |  |  | Client
| Carbon Benefits | NOT CERTAIN HOW TO QUANTIFY | benusrcard | float | € | DS | AN |  |  | Client
| Other Benefits |  | benusrmisc | float | € | DT | AO |  |  | Client
| Emissions avoided at the Heat Offtaker |  | benusremit | float | € | DU |  |  |  | Client
| Energy savings certificates (or equivalent) For Offtaker |  | benusrnrg | float | € | DV |  |  |  | Client
| Offtaker Cost of Maintenance | Annual maintenance cost SPECIFIC TO THIS HEAT SYSTEM | cstusrmnt | float | € | DW
| External Offtaker equipment costs |  | cstustext | float | € | DX |  |  |  | Client
| Costs of Storage Equipment |  | cstusrsto | float | € | DY | CI |  |  | Client
| Ancillary Heat Offtaker Equipment Costs |  | cstushteq | float | € | DZ | CH |  |  | Client
TENANT BUSINESS COSTS/BENEFITS | incomplete |  | n |  |  | EA |  |  |  | Client
| Advanced Cooling Capacity | NOT CERTAIN HOW TO QUANTIFY | benitcool | float |  | EB |  |  |  | Client
| Cost of cooling energy (IT facility) |  | cstitcool | float | € | EC |  |  |  | Client
| incomplete |  | n |  |  | ED |  |  |  | Client
| incomplete |  | n |  |  | EF |  |  |  | Client
OWNER BUSINESS BENFITS | Emissions Avoided at the IT facility |  | avdemit | float | € | EP |  |  |  | Client
| Water Usage Avoidance |  | avdh20 | float | € | EQ |  |  |  | Client
| Earnings from selling the heat | Where Offtaker pays for reused heat, at what RATE? | heatrev | float | € | ER |  |  |  | Client
| Energy savings certificates (or equivalent) IT facility |  | nrgcerts | float | € | ES |  |  |  | Client
| Savings Associated to Avoided Equipment |  | avdeqpt | float | € | ET |  |  |  | Client
| Subsidies |  | subs | float | € | EU |  |  |  | Client
| Emissions Costs Avoided |  | avdemtcst | float | € | EV |  |  |  | Client
| Tax rebates |  | avdtax | float | € | EW |  |  |  | Client
| incomplete |  | n |  |  | EX |  |  |  | Client
| incomplete |  | n |  |  | EY |  |  |  | Client
| incomplete |  | n |  |  | EZ |  |  |  | Client
CONSTRUCTION / INSTALLATION COSTS | Costs of Planning | Costs associated with the development of the project | costplan | float | € | FA | CL |  |  | Client
| Costs of Permitting and Compliance | Costs associated with securing permits, and complying with any jurisdictional regulations | costperm | float | € | FB |  |  |  | Client
| Costs of Architects | Costs of engaging architects as required | costarch | float | € | FC |  |  |  | Client
| Costs of Engineering | Costs of engaging engineers as required | costeng | float | € | FD | CM |  |  | Client
| incomplete |  | n |  |  | FE |  |  |  | Client
| Cost of Equipment | Costs for the major equipment of Heat Reuse | costmjeq | float | € | FF | CF |  |  | Client
| Heat-exchanging room elements | Ancillary Equipment at Owner space | costmneq | float | € | FG |  |  |  | Client
| Installation Costs | the costs of installing the major equipment within the Owners site, exclusice of piping. | cstinslpip | float | € | FH |  |  |  | Client
| Costs of Controls | The sum of all electronic monitoring and controlling devices, including one local "PLC" | costcntrl | float | € | FI |  |  |  | Client
| Electrical Installation | The cost for the installation of both power wiring to the system, and conttrols installation and wiring. | cstelcinst | float | € | FJ |  |  |  | Client
| Piping Diameter (IT Side) | The pipe size of the majority of the headers | pipitdia | int | mm | FK | BY |  |  | Client
| Piping Length (IT Side) | The total length of Heat Reuse piping on the IT side of the system | pipitlen | int | m | FL | BZ |  |  | Client
| Piping Insulation (IT Side) | Thickness of the pipe insulation | pipitins | int | mm | FM | CA |  |  | Client
| Cost of Piping on the IT side | The costs of installing the IT Cooling piping | costpipit | float | € | FN |  |  | (calculated) | Engine
| Piping Diameter (Heat Offtaker Side) | The pipe size of the majority of the headers | pipusdia | int | mm | FU | CB |  |  | Client
| Piping Length (Heat Offtaker Side) | The total length of Heat Reuse piping on the IT side of the system | pipuslen | int | m | FV | CC |  |  | Client
| Piping Insulation (Heat Offtaker Side) | thickness of the pipe insulation | pipusins | int | mm | FQ | CD |  |  | Client
| Cost of piping on the Offtaker Side, within Owner boundary | Cost to install the Offtaker piping, on Owner site | costpipusr | float | € | FR |  |  | (calculated) | Engine
| Valves and Fittings | An estimation of the ancillary piping devices | costvalit | float | € | FS |  |  | (calculated) | Engine
| Valves and Fittings | An estimation of the ancillary piping devices | costvalusr | float | € | FT |  |  | (calculated) | Engine
| Cost of Piping | The sum of all the piping installation costs | costpipe | float | € | FO | CE | = FN + FR + FS + FT | (calculated) | Engine
| Ancillary IT Facility Costs | Miscellaneous costs to accommodate the system | costanceq | float | € | FP | CG |  |  | Client
| Civil works associated | All cumulative costs to install the infrastructure, NOT within the Owner or Offtaker boundaries | costcvl | float | € | FW |  |  |  | Client
| Weight bearing elements | Facility structural costs | coststct | float | € | FX |  |  |  | Client
| The cost of installing the Heat Reuse System | Costs of installation, incurred at the Owners site | costinst | float | € | FY |  |  |  | Client
| What was the cost of the IT facility or data centre? | What is the reported value of the IT Facility? | costitctr | float | € | FZ | AI |  |  | Client
OWNER OPERATING COSTS | Space costs | The value of the real estate occupied by the heat reuse equipment | spaceval |  |  | GA |  |  |  | Client
| Energy usage for chillers | The cost of operating chillers, to replace the heat rejection of heat to the Offtaker | costchlr |  |  | GB |  |  |  | Client
| Energy usage for free-cooling | The cost of operating an alternate cooling strategy, to replace the heat rejection of heat to the Offtaker | costfrec |  |  | GC |  |  |  | Client
| Maintenance of the Heat Transfer System | Annual cost to maintain the system | costmaint |  |  | GD |  |  |  | Client
| incomplete |  | n |  |  | GE |  |  |  | Client
| incomplete |  | n |  |  | GF |  |  |  | Client
| incomplete |  | n |  |  | GG |  |  |  | Client
| incomplete |  | n |  |  | GH |  |  |  | Client
| incomplete |  | n |  |  | GI |  |  |  | Client
| incomplete |  | n |  |  | GJ |  |  |  | Client
| incomplete |  | n |  |  | GK |  |  |  | Client
| incomplete |  | n |  |  | GL |  |  |  | Client
| incomplete |  | n |  |  | GM |  |  |  | Client
| incomplete |  | n |  |  | GN |  |  |  | Client
| incomplete |  | n |  |  | GO |  |  |  | Client
| incomplete |  | n |  |  | GP |  |  |  | Client
| incomplete |  | n |  |  | GQ |  |  |  | Client
| incomplete |  | n |  |  | GR |  |  |  | Client
COMMON | Boundary definition |  | bounds | string | n/a | EG |  | HX Flanges | 500 CHAR | Client
| Discount Rate (for NPV = 0) |  | r | float | % | EH |  | 0.03 | 0.001 - 0.10 | Client
| incomplete |  | n |  |  | EI |  |  |  | Client
| Amortization time |  | T | float | years | EJ |  | 20 | .5 - 40.0 | Client
| incomplete |  | n |  |  | EK |  |  |  | Client
| incomplete |  | n |  |  | EL |  |  |  | Client
| incomplete |  | n |  |  | EM |  |  |  | Client
| incomplete |  | n |  |  | EN |  |  |  | Client
| incomplete |  | n |  |  | EO |  |  |  | Client
BOTTOM LINE | What was the cost to implement Heat Reuse? | The sum of all construction and project costs, before operations, by all parties, not including any offsets. | costproj | float | € | GS | AJ | (calculated) |  | Engine
| What will be the anticipated Operating Cost for one year? | Based on performance of the systems as rated, presuming fully loaded IT, and full heat utilization by the Offtaker system. | costoper | float | € | GT |  | (calculated) |  | Engine
| What is the sum of all direct incentives? | The sum of all rebates, bonuses, offsets, etc. | sumoffset | float | € | GU |  | (calculated) |  | Engine
| incomplete |  | n |  | € | GV |  | (calculated) |  | Engine
| incomplete |  | n |  | € | GW |  | (calculated) |  | Engine
| IRR |  | IRR | float | € | GX |  | (calculated) |  | Engine
| NPV |  | NPV | float | € | GY |  | (calculated) |  | Engine
| Net Return on Investment |  | ROI | float | € | GZ |  | (calculated) |  | Engine
| Net Economical Impact of this Heat Reuse System, for the first year? |  | impactyr | float | € | HA |  | (calculated) |  | Engine
| Net Economical Impact of this Heat Reuse System, for the Project Life? |  | impactlif | float | € | HB |  | (calculated) |  | Engine
EXTERNAL REFERENCES (there will be several more) | 1/2" Pipe By Length | THESE WILL BE THE CURRENT, ACTIVE PRICE per meter FOR PIPING, AT TIME OF CLIENT INPUT. WE WILL NEED TO CONFIRM ON WHICH PIPE STANDARD TO ANTICIPATE USAGE | pipprc1_2 | float | € | HC | SHOWN ONLY IN SUB-APP | (calculated) |  | External
| 3/4" Pipe By Length |  | pipprc3_4 | float | € | HD |  | (calculated) |  | External
| 1" Pipe By Length |  | pipprc1 | float | € | HE |  | (calculated) |  | External
| 2" Pipe By Length |  | pipprc2 | float | € | HF |  | (calculated) |  | External
| 4" Pipe By Length |  | pipprc4 | float | € | HG |  | (calculated) |  | External
| 6" Pipe By Length |  | pipprc6 | float | € | HH |  | (calculated) |  | External
| 8" Pipe By Length |  | pipprc8 | float | € | HI |  | (calculated) |  | External
| 10" Pipe By Length |  | pipprc10 | float | € | HJ |  | (calculated) |  | External
| 12" Pipe By Length |  | pipprc12 | float | € | HK |  | (calculated) |  | External
| 14" Pipe By Length |  | pipprc14 | float | € | HL |  | (calculated) |  | External
| 16" Pipe By Length |  | pipprc16 | float | € | HM |  | (calculated) |  | External
| 1/2" Valve Package |  | valprc1_2 | float | € | HN |  | (calculated) |  | External
| 3/4" Valve Package |  | valprc3_4 | float | € | HO |  | (calculated) |  | External
| 1" Valve Package |  | valprc1 | float | € | HP |  | (calculated) |  | External
| 2" Valve Package |  | valprc2 | float | € | HQ |  | (calculated) |  | External
| 4" Valve Package |  | valprc4 | float | € | HR |  | (calculated) |  | External
| 6" Valve Package |  | valprc6 | float | € | HS |  | (calculated) |  | External
| 8" Valve Package |  | valprc8 | float | € | HT |  | (calculated) |  | External
| 10" Valve Package |  | valprc10 | float | € | HU |  | (calculated) |  | External
| 12" Valve Package |  | valprc12 | float | € | HV |  | (calculated) |  | External
| 14" Valve Package |  | valprc14 | float | € | HW |  | (calculated) |  | External
| 16" Valve Package |  | valprc16 | float | € | HX |  | (calculated) |  | External
KW
KX
KY
| Standard Instrument and Controls Package | The total cost of the typical package of pressure, temperature, and flow instrumentation and associated controls package | cduinst | float | € | KZ |  | (calculated) |  | External
CLIENT Fluctuation INPUT | Hourly Fluctuation Factor for Computing for 0:00 | The percentage of Computing normally availalble | dvrit00 | float | % | IA | ONLY SHOWN AT CLIENT DATA INPUT PAGE | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 1:00 | The percentage of Computing normally availalble | dvrit01 | float | % | IB |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 2:00 | The percentage of Computing normally availalble | dvrit02 | float | % | IC |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 3:00 | The percentage of Computing normally availalble | dvrit03 | float | % | ID |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 4:00 | The percentage of Computing normally availalble | dvrit04 | float | % | IE |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 5:00 | The percentage of Computing normally availalble | dvrit05 | float | % | IF |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 6:00 | The percentage of Computing normally availalble | dvrit06 | float | % | IG |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 7:00 | The percentage of Computing normally availalble | dvrit07 | float | % | IH |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 8:00 | The percentage of Computing normally availalble | dvrit08 | float | % | II |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 9:00 | The percentage of Computing normally availalble | dvrit09 | float | % | IJ |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 10:00 | The percentage of Computing normally availalble | dvrit10 | float | % | IK |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 11:00 | The percentage of Computing normally availalble | dvrit11 | float | % | IL |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 12:00 | The percentage of Computing normally availalble | dvrit12 | float | % | IM |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 13:00 | The percentage of Computing normally availalble | dvrit13 | float | % | IN |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 14:00 | The percentage of Computing normally availalble | dvrit14 | float | % | IO |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 15:00 | The percentage of Computing normally availalble | dvrit15 | float | % | IP |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 16:00 | The percentage of Computing normally availalble | dvrit16 | float | % | IQ |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 17:00 | The percentage of Computing normally availalble | dvrit17 | float | % | IR |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 18:00 | The percentage of Computing normally availalble | dvrit18 | float | % | IS |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 19:00 | The percentage of Computing normally availalble | dvrit19 | float | % | IT |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 20:00 | The percentage of Computing normally availalble | dvrit20 | float | % | IU |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 21:00 | The percentage of Computing normally availalble | dvrit21 | float | % | IV |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 22:00 | The percentage of Computing normally availalble | dvrit22 | float | % | IW |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 23:00 | The percentage of Computing normally availalble | dvrit23 | float | % | IX |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for January | The percentage of Computing normally availalble | dvritjan | float | % | IY |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for February | The percentage of Computing normally availalble | dvritfeb | float | % | IZ |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for March | The percentage of Computing normally availalble | dvritmar | float | % | JA |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for April | The percentage of Computing normally availalble | dvritapr | float | % | JB |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for May | The percentage of Computing normally availalble | dvritmay | float | % | JC |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for June | The percentage of Computing normally availalble | dvritjun | float | % | JD |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for July | The percentage of Computing normally availalble | dvritjul | float | % | JE |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for August | The percentage of Computing normally availalble | dvritaug | float | % | JF |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for September | The percentage of Computing normally availalble | dvritsep | float | % | JG |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for October | The percentage of Computing normally availalble | dvritoct | float | % | JH |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for November | The percentage of Computing normally availalble | dvritnov | float | % | JI |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for December | The percentage of Computing normally availalble | dvritdec | float | % | JJ |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 0:00 | The percentage of heat used by Offtaker system | dvrusr00 | float | % | JK |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 1:00 | The percentage of heat used by Offtaker system | dvrusr01 | float | % | JL |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 2:00 | The percentage of heat used by Offtaker system | dvrusr02 | float | % | JM |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 3:00 | The percentage of heat used by Offtaker system | dvrusr03 | float | % | JN |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 4:00 | The percentage of heat used by Offtaker system | dvrusr04 | float | % | JO |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 5:00 | The percentage of heat used by Offtaker system | dvrusr05 | float | % | JP |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 6:00 | The percentage of heat used by Offtaker system | dvrusr06 | float | % | JQ |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 7:00 | The percentage of heat used by Offtaker system | dvrusr07 | float | % | JR |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 8:00 | The percentage of heat used by Offtaker system | dvrusr08 | float | % | JS |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 9:00 | The percentage of heat used by Offtaker system | dvrusr09 | float | % | JT |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 10:00 | The percentage of heat used by Offtaker system | dvrusr10 | float | % | JU |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 11:00 | The percentage of heat used by Offtaker system | dvrusr11 | float | % | JV |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 12:00 | The percentage of heat used by Offtaker system | dvrusr12 | float | % | JW |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 13:00 | The percentage of heat used by Offtaker system | dvrusr13 | float | % | JX |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 14:00 | The percentage of heat used by Offtaker system | dvrusr14 | float | % | JY |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 15:00 | The percentage of heat used by Offtaker system | dvrusr15 | float | % | JZ |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 16:00 | The percentage of heat used by Offtaker system | dvrusr16 | float | % | KA |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 17:00 | The percentage of heat used by Offtaker system | dvrusr17 | float | % | KB |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 18:00 | The percentage of heat used by Offtaker system | dvrusr18 | float | % | KC |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 19:00 | The percentage of heat used by Offtaker system | dvrusr19 | float | % | KD |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 20:00 | The percentage of heat used by Offtaker system | dvrusr20 | float | % | KE |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 21:00 | The percentage of heat used by Offtaker system | dvrusr21 | float | % | KF |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 22:00 | The percentage of heat used by Offtaker system | dvrusr22 | float | % | KG |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 23:00 | The percentage of heat used by Offtaker system | dvrusr23 | float | % | KH |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for January | The percentage of heat used by Offtaker system | dvrusrjan | float | % | KI |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for February | The percentage of heat used by Offtaker system | dvrusrfab | float | % | KJ |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for March | The percentage of heat used by Offtaker system | dvrusrmar | float | % | KK |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for April | The percentage of heat used by Offtaker system | dvrusrapr | float | % | KL |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for May | The percentage of heat used by Offtaker system | dvrusrmay | float | % | KM |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for June | The percentage of heat used by Offtaker system | dvrusrjun | float | % | KN |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for July | The percentage of heat used by Offtaker system | dvrusrjul | float | % | KO |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for August | The percentage of heat used by Offtaker system | dvrusraug | float | % | KP |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for September | The percentage of heat used by Offtaker system | dvrusrsep | float | % | KQ |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for October | The percentage of heat used by Offtaker system | dvrusroct | float | % | KR |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for November | The percentage of heat used by Offtaker system | dvrusrnov | float | % | KS |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for December | The percentage of heat used by Offtaker system | dvrusrdec | float | % | KT |  | 100% | 0 - 100% | Client
| Data Point Name | Data Point Description | Variable Name | Data Type | Units | DATA Table Column Location | VISUALIZATION Template Column Location | Default | Anticipated Range of Values | Source of Input Data
| 1/2" Standard Stop Valve Cost | Cost of Standard Ball Valve (e.g. gage stop) | vlstd1_2 | float | $ | LA | N/A | 0 | 10.00-100.00 | EXT. DATA
| 3/4" Standard Stop Valve Cost | Cost of Standard Ball Valve (e.g. drain valve) | vlstd3_4 | float | $ | LB | N/A | 17.35 | 10.00-100.00 | EXT. DATA
| 1" Standard Stop Valve Cost | Cost of Standard Ball Valve | vlstd1 | float | $ | LC | N/A | 0 | 10.00-100.00 | EXT. DATA
| 2" Standard Stop Valve Cost | Cost of Standard Butterfly Valve | vlstd2 | float | $ | LD | N/A | 0 | >100.00 | EXT. DATA
| 4" Standard Stop Valve Cost | Cost of Standard Butterfly Valve | vlstd4 | float | $ | LE | N/A | 0 | >100.00 | EXT. DATA
| 6" Standard Stop Valve Cost | Cost of Standard Butterfly Valve | vlstd6 | float | $ | LF | N/A | 0 | >100.00 | EXT. DATA
| 8" Standard Stop Valve Cost | Cost of Standard Butterfly Valve | vlstd8 | float | $ | LG | N/A | 0 | >100.00 | EXT. DATA
| 10" Standard Stop Valve Cost | Cost of Standard Butterfly Valve | vlstd10 | float | $ | LH | N/A | 0 | >100.00 | EXT. DATA
| 12" Standard Stop Valve Cost | Cost of Standard Butterfly Valve | vlstd12 | float | $ | LI | N/A | 0 | >100.00 | EXT. DATA
| 14" Standard Stop Valve Cost | Cost of Standard Butterfly Valve | vlstd14 | float | $ | LJ | N/A | 0 | >100.00 | EXT. DATA
| 16" Standard Stop Valve Cost | Cost of Standard Butterfly Valve | vlstd16 | float | $ | LK | N/A | 0 | >100.00 | EXT. DATA
| 1/2" Premium Stop Valve Cost | Cost of Stainless Steel Ball Valve (e.g. gage stop) | vlstls1_2 | float | $ | LL | N/A | 0 | 10.00-100.00 | EXT. DATA
| 3/4" Premium Stop Valve Cost | Cost of Stainless Steel Ball Valve (e.g. drain valve) | vlstls3_4 | float | $ | LM | N/A | 0 | 10.00-100.00 | EXT. DATA
| 1" Premium Stop Valve Cost | Cost of Stainless Steel Ball Valve | vlstls1 | float | $ | LN | N/A | 0 | 10.00-100.00 | EXT. DATA
| 2" Premium Stop Valve Cost | Cost of Stainless Steel Butterfly Valve | vlstls2 | float | $ | LO | N/A | 0 | >100.00 | EXT. DATA
| 4" Premium Stop Valve Cost | Cost of Stainless Steel Butterfly Valve | vlstls4 | float | $ | LP | N/A | 0 | >100.00 | EXT. DATA
| 6" Premium Stop Valve Cost | Cost of Stainless Steel Butterfly Valve | vlstls6 | float | $ | LQ | N/A | 0 | >100.00 | EXT. DATA
| 8" Premium Stop Valve Cost | Cost of Stainless Steel Butterfly Valve | vlstls8 | float | $ | LR | N/A | 0 | >100.00 | EXT. DATA
| 10" Premium Stop Valve Cost | Cost of Stainless Steel Butterfly Valve | vlstls10 | float | $ | LS | N/A | 0 | >100.00 | EXT. DATA
| 12" Premium Stop Valve Cost | Cost of Stainless Steel Butterfly Valve | vlstls12 | float | $ | LT | N/A | 0 | >100.00 | EXT. DATA
| 14" Premium Stop Valve Cost | Cost of Stainless Steel Butterfly Valve | vlstls14 | float | $ | LU | N/A | 0 | >100.00 | EXT. DATA
| 16" Premium Stop Valve Cost | Cost of Stainless Steel Butterfly Valve | vlstls16 | float | $ | LV | N/A | 0 | >100.00 | EXT. DATA
| 1/2" Air Vent Valve Cost | Cost of Automatic Air Vent Valve | vlvnt1_2 | float | $ | LW | N/A | 0 | 10.00-100.00 | EXT. DATA
| 3/4" Pressure Relief Valve Cost | Cost of Pressure Relief Valve | vlrelf3_4 | float | $ | LX | N/A | 0 | 10.00-100.00 | EXT. DATA
| 1" Control Valve Cost | Cost of Standard Control Valve, 24 volt, 4-20ma | vlctrl1 | float | $ | LY | N/A | 0 | >100.00 | EXT. DATA
| 2" Control Valve Cost | Cost of Standard Control Valve, 24 volt, 4-20ma | vlctrl2 | float | $ | LZ | N/A | 0 | >100.00 | EXT. DATA
| 4" Control Valve Cost | Cost of Standard Control Valve, 24 volt, 4-20ma | vlctrl4 | float | $ | MA | N/A | 0 | >100.00 | EXT. DATA
| 6" Control Valve Cost | Cost of Standard Control Valve, 24 volt, 4-20ma | vlctrl6 | float | $ | MB | N/A | 0 | >100.00 | EXT. DATA
| 8" Control Valve Cost | Cost of Standard Control Valve, 120 volt, 4-20ma | vlctrl8 | float | $ | MC | N/A | 0 | >100.00 | EXT. DATA
| 10" Control Valve Cost | Cost of Standard Control Valve, 120 volt, 4-20ma | vlctrl10 | float | $ | MD | N/A | 0 | >100.00 | EXT. DATA
| 12" Control Valve Cost | Cost of Standard Control Valve, 120 volt, 4-20ma | vlctrl12 | float | $ | ME | N/A | 0 | >100.00 | EXT. DATA
| 14" Control Valve Cost | Cost of Standard Control Valve, 120 volt, 4-20ma | vlctrl14 | float | $ | MF | N/A | 0 | >100.00 | EXT. DATA
| 16" Control Valve Cost | Cost of Standard Control Valve, 120 volt, 4-20ma | vlctrl16 | float | $ | MG | N/A | 0 | >100.00 | EXT. DATA
Degrees

## Data DICTIONARY 3a (hidden)
| Data Point Name | Data Point Description | Short Name (for formulas, ect.) | Data Type | Units | DATA Table Column Location | VISUALIZATION Template Column Location | Default | Anticipated Range of Values | Source of Input Data | THE CELLS IN COLUMN "N" ARE OPEN FOR LINE-BY-LINE COMMENTS AND FEEDBACK
INTRODUCTORY INFORMATION | Index | Identifier for each unique Record | index | int |  | A | A | n | 1 - 5000 | Engine
| Data Source | Source that the data was gathered from | source | string | n/a | D | B | Client | 30 char | Engine
| Party Inputting the Data, per Record | Regardless of existing or new record, the common name for "where did it come from" | Client | string | n/a | C |  | Client | 30 char | Client
| Site Name | The "Common" name for the site | name | string | n/a | B | C | n/a | 50 char | Client
| Date of given data | Date of entry of the data | date1 | Date | 2023-12-31 | E | D | 2023-12-31 | date | Client
| Date of latest update | Date of last update of the data | date2 | Date | 2023-12-31 | F |  | 2023-12-31 | date | Client
| City of the site | Nearest City to the site location | city | string | n/a | G | E | n/a | 30 char | Client
| State | State or region of the site location | state | string | n/a | H |  | n/a | 30 char | Client
| Country of the site | Country of the location | country | string | n/a | I | F | n/a | 30 char | Client
| IT Facility Latitude | Geographical Latitude of the site | sitelat | float | decimal degrees | J |  | n/a | -80.000000 to 80.000000 | Client
| IT Facility Longitude | Geographical Longitude of the site | sitelong | float | decimal degrees | K |  | n/a | -180.000000 to 180.000000 | Client
| Heat Offtaker Latitude | Geographical Latitude of the heat Offtaker | userlat | float | decimal degrees | L |  | n/a | -80.000000 to 80.000000 | Client
| Heat Offtaker Longitude | Geographical Longitude of the heat Offtaker | userlong | float | decimal degrees | M |  | n/a | -180.000000 to 180.000000 | Client
| Site Owner | Principal owner of the Data Facility | siteowner | string | n/a | N |  | n/a | 100 char | Client
| Site Owner Website or Links | Any online information regarding site owners | soweblink | hyperlink | n/a | O | AF | n/a | url | Client
| Data Centre Principal Tenant or User | Principal tenant or user of the site | ituser | string | n/a | P |  | = siteowner | 100 char | Client
| Data Centre Space Size (m2) | Footprint area of the white space | warea | float | square meters | Q | AL | n/a | 100 to 9999 | Client
| Data Centre Racks Size | The number of data cabinets of racks | rack | int | count | R | AM | n/a | 1 to 100000 | Client
| IT Power Per Rack | The avaerage amount of power per standard rack | rackkw | float | kiloWatts | S |  | n/a | 1 to 300 | Client
| Tenant Website or Links | Any online information regarding tenants or users of the data centre | itweblink | hyperlink | n/a | T | AG | n/a | url | Client
| Heat Offtaker System Owner | Principal owner of the Heat Offtaker System | huowner | string | n/a | U |  | n/a | 100 char | Client
| Heat Offtaker Owner Website or Links | Any online information regarding the owner/operator of the heat Offtaker system | howeblink | hyperlink | n/a | V | AO | n/a | url | Client
| Heat Offtaker Principal Offtaker | Principal Offtaker of the heat | hruser | string | n/a | W |  | =huowner | 100 char | Client
| Heat Offtaker Website or Links | Any online information regarding the actual Offtaker(s) of the heat | huweblink | hyperlink | n/a | X | AP | n/a | url | Client
| Type of Offtaker | General category of heat Offtaker | usertype | string | n/a | Y | AE | SELECTION BOX: | 30 char | Client
| What is the Business structure? | Short explanation of the relationship between the It Facility and the Heat Offtaker | relationship | string | n/a | Z | AD | n/a | 250 char | Client
| When did heat reuse start? |  | date3 | Date | 2023-12-31 | AA | AC | 2023-12-31 | date | Client
| Is there a product resulting from the heat reuse? | What does the Heat Offtaker get from the use of the heat, if there is an "industrial" Offtaker? | product | string | n/a | AB | AH | No | 250 char | Client
| Data Centre Throughput | What is the size of the computing equipment, in "Computing Terms" | datasize | float | pflops | DA |  | n/a |  | Client
DATA HALL STUFF | How much of the IT Equipment is Cooled by Air ("traditional") (%) |  | itaircl | float |  | DB | Y | n/a | <1.0 | Client
| How much of the IT Equipment is Cooled by Rack Door Heat Exchanger (%) |  | itdrcl | float |  | DC | Z | n/a | <1.0 | Client
| How much of the IT Equipment is Cooled by "Direct-to-Chip" Cold Plate (%) |  | itchipcl | float |  | DD | AA | n/a | <1.0 | Client
| How much of the IT Equipment is Cooled by "Other" Cold Plate (%) |  | itpltcl | float |  | DE |  | n/a | <1.0 | Client
| How much of the IT Equipment is Cooled by Single Phase Immersion (%) |  | it1imm | float |  | DF | AB | n/a | <1.0 | Client
| How much of the IT Equipment is Cooled by Two Phase Immersion (%) |  | it2imm | float |  | DG | AB | n/a | <1.0 | Client
| Data Centre Load Daily Fluctuation | Daily swing in available heat, from Client input | itdivrday | float |  | DH |  | 1 | (calculated) | Engine
| Data Centre Load Annual Fluctuation | Annual swing in available heat, from Client input | itdvryr | float |  | DI |  | 1 | (calculated) | Engine
| Waste Heat Available, Adjusted for Fluctuation | Total Waste Heat Available, multiplied by both Fluctuation factors | whadvr | float |  | DJ |  | =wha | (calculated) | Client
| RESERVED |  | n |  |  | DK |  |  |  | Client
| RESERVED |  | n |  |  | DL |  |  |  | Client
ENERGY INFORMATION | Installed power of the site | Installed power of the site | sitepwr | float | MegaWatts | AC | G | n/a | 0.0 - 500.0 | Client
| Rated data Centre power | Rated data Centre power | itpwr | float | MegaWatts | AD | H | n/a | 0.0 - 500.0 | Client
| Primary Electrical Power Source | Primary Electrical Power Source | pwrsce1 | string | n/a | AE |  | n/a | 50 char | Client
| Primary Source Type | Primary Source Type | pwrtype1 | string | n/a | AF | AP | n/a | 50 char | Client
| Base Cost Rate for Primary Power | Base Cost Rate for Primary Power | pwrrate1 | float | FORMAT?? | AG |  | n/a |  | Client
| Rate Adjustments to Power Base Rate | Rate Adjustments to Power Base Rate | pwrrate1ad | float | n/a | AH |  | n/a |  | Client
| Proportion of Total Power From Primary Source | Proportion of Total Power From Primary Source | pwr1prop | float | n/a | AI |  | 1 | 0 - 1.0 | Client
| Secondary Power Source | Secondary Power Source | pwrsce2 | string | n/a | AJ |  | n/a | 50 char | Client
| Secondary Source Type | Secondary Source Type | pwrtype2 | string | n/a | AK |  | n/a | 50 char | Client
| Base Cost Rate for Secondary Power | Base Cost Rate for Secondary Power | pwrrate2 | float | FORMAT?? | AL |  | n/a |  | Client
| Rate Adjustments to Secondary Power Base Rate | Rate Adjustments to Secondary Power Base Rate | pwrrate2ad | float | FORMAT?? | AM |  | n/a |  | Client
| Proportion of Total Power From Secondary Source | Proportion of Total Power From Secondary Source | pwrrate2prop | string | n/a | AN |  | n/a |  | Client
| Alternate or Additional Fuels | Alternate or Additional Fuels | pwralt | string | n/a | AO |  | n/a |  | Client
| Alternalte Fuel Type | Alternalte Fuel Type | pwralttype | string | n/a | AP |  | n/a |  | Client
| Base Cost rate for Alternate or Additional Fuels | Base Cost rate for Alternate or Additional Fuels | pwrratealt | float | n/a | AQ |  | n/a |  | Client
| Rate Adjustments to Alternate Fuels Base Cost Rate | Rate Adjustments to Alternate Fuels Base Cost Rate | pwrratealtad | float | n/a | AR |  | n/a |  | Client
| Water Usage | Water Usage | h2ouse | float | liters per year | AS | CR | 0 |  | Client
| Water cost rate | Water cost rate | h2orate | float | FORMAT?? | AT | CS | 0 |  | Client
| Is the Heat Offtaker Within the building? | Is the Heat Offtaker Within the building? | usebldg | string | Yes / No | AU | O | No | Yes / No | Client
| Is the Heat Offtaker Within the Campus? | Is the Heat Offtaker Within the Campus? | usecamp | string | Yes / No | AV | P | Yes | Yes / No | Client
| Is the Heat Offtaker Off premises? | Is the Heat Offtaker Off premises? | useprem | string | Yes / No | AW | Q | Yes | Yes / No | Client
| Distance to the Heat Offtaker | When Offtaker is off-premises, how far to the first Offtaker | usedist | int | meters | AX | R | 0 | 0 to 5000 | Client
| Energy Reuse Effectiveness (ERE) | Use these figures if offered by Client | ere | float | none | AY | U |  | 0 <1.0 | Client
| Energy Reuse Factor (ERF) | Use these figures if offered by Client | erf | float | none | AZ | V |  | 0 <1.0 | Client
| Heat Reuse Effectiveness (HRE) | Use these figures if calculated within our engine | hre | float | none | BA |  | (calculated) | 0 <1.0 | Engine
| Heat Reuse Factor (HRF) | Use these figures if calculated within our engine | hrf | float | none | BB |  | (calculated) | 0 <1.0 | Engine
| Percentage of Heat Reused | Use these figures if offered by Client | hrec | float | % | BC | W |  | 0 <1.0 | Client
| Amount of Heat Reused | Use these figures if offered by Client | hrfc | float | MW | BD | X |  | 0 <1.0 | Client
| Total Heat Available | Heat made available from the IT System | wha | float | MW | BE |  | (calculated) | 0.0 to 5000.0 | Engine
| Total Heat Reused | Heat actually processed by Offtaker system | uhr | float | MW | BF |  | (calculated) | 0.0 to 5000.0 | Engine
| Total Heat Reused, Adjusted for Fluctuation | Total Heat multiplied by both Fluctuation factors | uhrdvrad | float | MW | BG |  | (calculated) | 0.0 to 5000.0 | Engine
| HRE, Adjusted for Fluctuation | Hre, adjusted by all four factors | hredvrad | float | MW | BH |  | (calculated) | 0.0 to 5000.0 | Engine
MECHANICAL OPERATING PARAMETERS | Electrical Power to operate IT Medium stream | Mostly, will be the pump power | pwrf1 | float | kW | BI |  | 25 | 1.0 - 500.0 | Client
| Typical temperature of cooling Medium to the IT equipment (Min) | Typical temperature of cooling Medium to the IT equipment (Min) | T1min | float | Degrees (C) | BJ | I | 10 | 10.0 - 40.0 | Client
| Typical temperature of cooling Medium to the IT equipment (Max) | Typical temperature of cooling Medium to the IT equipment (Max) | T1max | float | Degrees (C) | BK | J | 40 | 10.0 - 40.0 | Client
| Rated temperature of cooling Medium to the IT equipment | Rated temperature of cooling Medium to the IT equipment | T1 | float | Degrees (C) | BL | BG | 30 | 10.0 - 40.0 | Client
| Typical temperature of cooling Medium from the IT equipment (Min) | Typical temperature of cooling Medium from the IT equipment (Min) | T2min | float | Degrees (C) | BM | K | 20 | 10.0 - 70.0 | Client
| Typical temperature of cooling Medium from the IT equipment (Max) | Typical temperature of cooling Medium from the IT equipment (Max) | T2max | float | Degrees (C) | BN | L | 60 | 10.0 - 70.0 | Client
| Rated temperature of cooling Medium from the IT equipment | Rated temperature of cooling Medium from the IT equipment | T2 | float | Degrees (C) | BO |  | 40 | 10.0 - 70.0 | Client
| Temperature difference across IT side of heat exchanger | Temperature difference across IT side of heat exchanger | itdt | float | Degrees (C) | BP |  | (calculated) | 10.0 - 70.0 | Engine
| Medium used in the IT Cooling Circuit | What is the medium being used for capturing heat from the IT system? | fluid1 | string | n/a | BQ | AR | Water |  | Client
| Medium pressure entering the Heat Exchanger on the IT Cooling Side | Gauge Pressure at the Heat Exchanger | P2 | float | bar | BR | AW | 4.0 | 1.0 - 25.0 | Client
| Medium Pressure leaving the Heat Exchanger on the IT Cooling Side | Gauge Pressure at the Heat Exchanger | P1 | float | bar | BS | AX | 1.0 | 1.0 - 25.0 | Client
| Medium Pressure drop across heat exchanger on IT side | Heat Exchanger "Delta P", on the IT Side | dpit | float | bar | BT |  | (calculated) |  | Engine
| Medium Flow in the IT Cooling Circuit | Fluid flow of IT Cooling Medium | F1 | float | Liters per Minute | BU | AY |  | 250 - 10000 | Client
| Fluid Viscosity in IT Cooling Circuit | Viscosity of IT Cooing Medium | fluid1vis | float | n/a | BV | AU | n/a |  | Client
| Heat Capacity of IT Cooling Medium | Heat Capacity of IT Cooling Medium | fluid1hc | float | n/a | BW |  | n/a |  | Client
| GWP of IT Cooling Medium | GWP of IT Cooling Medium | gwp1 | float | n/a | BX | AS | n/a |  | Client
| ODP of IT Cooling Medium | ODP of IT Cooling Medium | odp1 | float | n/a | BY | AT | n/a |  | Client
| Typical temperature of Medium returning from the Heat Offtaker (Min) | Typical temperature of Medium returning from the Heat Offtaker (Min) | T4min | float | Degrees (C) | BZ |  | 20 | 10.0 - 40.0 | Client
| Typical temperature of Medium returning from the Heat Offtaker (Max) | Typical temperature of Medium returning from the Heat Offtaker (Max) | T4max | float | Degrees (C) | CA |  | 40 | 10.0 - 50.0 | Client
| Rated temperature of Medium FROM the Heat Offtaker | Rated temperature of Medium FROM the Heat Offtaker | T4 | float | Degrees (C) | CB |  | 25 | 10.0 - 50.0 | Client
| Typical temperature of Medium To the Heat Offtaker (Min) | Typical temperature of Medium To the Heat Offtaker (Min) | T3min | float | Degrees (C) | CC | M | 30 | 10.0 - 60.0 | Client
| Typical temperature of Medium To the Heat Offtaker (Max) | Typical temperature of Medium To the Heat Offtaker (Max) | T3max | float | Degrees (C) | CD | N | 50 | 10.0 - 60.0 | Client
| Rated temperature of Medium TO the Heat Offtaker | Rated temperature of Medium TO the Heat Offtaker | T3 | float | Degrees (C) | CE |  | 45 | 10.0 - 60.0 | Client
| Temperature Difference across Offtaker side of heat exchanger | Temperature Difference across Offtaker side of heat exchanger | userdt | float | Degrees (C) | CF |  | (calculated) | 10.0 - 70.0 | Engine
| Medium used in the Heat Offtaker Circuit | What is the medium being used for heating? | fluid2 | string | n/a | CG | BE | Water | 50 char | Client
| Medium pressure entering the heat exchnager on the Heat Offtaker Side | Gauge Pressure at the Heat Exchanger | P4 | float | bar | CH |  | 5 | 1.0 - 25.0 | Client
| Medium Pressure leaving the heat exchanger on the Heat Offtaker Side | Gauge Pressure at the Heat Exchanger | P3 | float | bar | CI |  | 3 | 1.0 - 25.0 | Client
| Medium Pressure drop across heat exchanger on Offtaker side | Heat Exchanger "Delta P", on the Offtaker Side | dpuser | float | bar | CS |  | (calculated) |  | Engine
| Medium Flow in the Heat Offtaker Circuit | What is the fluid flow in the Offtaker side? | F2 | float | Liters per Minute | CJ | BL |  |  | Client
| Fluid Viscosity in Heat Offtaker Circuit | What is the viscosity of the Medium on the Offtaker side? | fluid2vis | float |  | CL | BF |  |  | Client
| Heat Capacity of Heat Offtaker Medium | What is the Heat Capacity of the Offtaker side Medium? | fluid2hc | float |  | CM | BG |  |  | Client
| Is there SHORT TERM thermal storage of the heated Medium? | If there is some kind of buffer tank? | storst | string | Yes / No | CN | BM | No | Yes / No | Client
| Size of the short term storage | How much Medium is stored or buffered? | storstsz | float |  | CO |  |  |  | Client
| Type of Short Term Storage | What type of storage is there? | storsttyp | string | n/a | CP |  | Tank | 50 char | Client
| Is there LONG TERM thermal storage of the heated Medium? | If there is a reservior or large body of water? | storlt | string | Yes / No | CQ | BN | No | Yes / No | Client
| Size of the long term storage | What is the volume of the large, long term storage? | storltsz | float |  | CR |  |  |  | Client
| Type of Long Term Storage | What type of storage is there? | storlttyp | string | n/a | CT |  | Reservior | 50 char | Client
| Is extra equipment required to Elevate temperatures? | If the Offtaker side Medium is not suffiently warm enough for the Offtaker's benefit, how is it further heated? | boost | string | Yes / No | CK | AB | No | Yes / No | Client
| What Equipment Type? | What is used to make the temperature "usable"? | boosteqp | string | n/a | CU |  | Heat Pump | "Heat Pump", "Boiler" | Client
| Heat Pump COP | IF a heat pump is used, how efficient is that heat pump? | bsthpcop | float | n/a | CV | AC |  | 0.5 - 1.0 | Client
| Boiler Efficiency | IF a boiler is used, how efficient is that boiler? | bstblreff | float | n/a | CW |  |  | 0.5 - 1.0 | Client
| Electrical Power to operate Offtaker Medium stream | Power for fluid movment on the Heat Offtaker side | pwrf2 | float | kW | CX |  | 25 | 1.0 - 1000.0 | Client
| Offtaker Daily Fluctuation Factor | Calculated from Client Input, DAILY swing in Usage | dvrusrday | float | n/a | CY |  | 1 | (calculated) | Engine
| Offtaker Seasonal Fluctuation Factor | Calculated from Client Input, ANNUAL swing in Usage | dvrusryr | float | n/a | CZ |  | 1 | (calculated) | Engine
Offtaker BUSINESS COSTS/BENEFITS | Offtaker Industrial Product 1 | Is there an industrial use for the heat? If so, what is the primary product? | prod1 | string |  | DM | AH | No | 100 char | Client
| Offtaker Product 1 Annual Revenue | Annual revenue to Offtaker from Product 1 | prod1rev | float | € | DN |  | 0 | 0 | Client
| Offtaker Industrial Product 2 | Is there an industrial use for the heat? If so, what is the secondary product? | prod2 | string |  | DO |  | No | 100 char | Client
| Offtaker Product 2 Annual Revenue | Annual revenue to Offtaker from Product 2 | prod2rev | float | € | DP |  | 0 | 0 | Client
| Offtaker Cost of Alternative Heat | What would heat cost RATE if there were no reuse? | althtrate | float | € | DQ |  |  |  | Client
| Cost of electricity (Offtaker) |  | usrpwrrate | float | € | DR |  |  |  | Client
| Carbon Benefits | NOT CERTAIN HOW TO QUANTIFY | benusrcard | float | € | DS | AN |  |  | Client
| Other Benefits |  | benusrmisc | float | € | DT | AO |  |  | Client
| Emissions avoided at the Heat Offtaker |  | benusremit | float | € | DU |  |  |  | Client
| Energy savings certificates (or equivalent) For Offtaker |  | benusrnrg | float | € | DV |  |  |  | Client
| Offtaker Cost of Maintenance | Annual maintennace cost SPECIFIC TO THIS HEAT SYSTEM | cstusrmnt | float | € | DW
| External Offtaker equipment costs |  | cstustext | float | € | DX |  |  |  | Client
| Costs of Storage Equipment |  | cstusrsto | float | € | DY | CI |  |  | Client
| Ancillary Heat Offtaker Equipment Costs |  | cstushteq | float | € | DZ | CH |  |  | Client
TENANT BUSINESS COSTS/BENEFITS | incomplete |  | n |  |  | EA |  |  |  | Client
| Advanced Cooling Capacity | NOT CERTAIN HOW TO QUANTIFY | benitcool | float |  | EB |  |  |  | Client
| Cost of cooling energy (IT facility) |  | cstitcool | float | € | EC |  |  |  | Client
| incomplete |  | n |  |  | ED |  |  |  | Client
| incomplete |  | n |  |  | EF |  |  |  | Client
OWNER BUSINESS BENFITS | Emissions Avoided at the IT facility |  | avdemit | float | € | EP |  |  |  | Client
| Water Usage Avoidance |  | avdh20 | float | € | EQ |  |  |  | Client
| Earnings from selling the heat | Where Offtaker pays for reused heat, at what RATE? | heatrev | float | € | ER |  |  |  | Client
| Energy savings certificates (or equivalent) IT facility |  | nrgcerts | float | € | ES |  |  |  | Client
| Savings Associated to Avoided Equipment |  | avdeqpt | float | € | ET |  |  |  | Client
| Subsidies |  | subs | float | € | EU |  |  |  | Client
| Emissions Costs Avoided |  | avdemtcst | float | € | EV |  |  |  | Client
| Tax rebates |  | avdtax | float | € | EW |  |  |  | Client
| incomplete |  | n |  |  | EX |  |  |  | Client
| incomplete |  | n |  |  | EY |  |  |  | Client
| incomplete |  | n |  |  | EZ |  |  |  | Client
CONSTRUCTION / INSTALLATION COSTS | Costs of Planning | Costs associated with the development of the project | costplan | float | € | FA | CL |  |  | Client
| Costs of Permitting and Compliance | Costs associated with securing permits, and complying with any jurisdictional regulations | costperm | float | € | FB |  |  |  | Client
| Costs of Architects | Costs of engaging architects as required | costarch | float | € | FC |  |  |  | Client
| Costs of Engineering | Costs of engaging engineers as required | costeng | float | € | FD | CM |  |  | Client
| incomplete |  | n |  |  | FE |  |  |  | Client
| Cost of Equipment | Costs for the major equipment of Heat Reuse | costmjeq | float | € | FF | CF |  |  | Client
| Heat-exchanging room elements | Ancillary Equipment at Owner space | costmneq | float | € | FG |  |  |  | Client
| Installation Costs | the costs of installing the major equipment within the Owners site, exclusice of piping. | cstinslpip | float | € | FH |  |  |  | Client
| Costs of Controls | The sum of all electronic monitoring and controlling devices, including one local "PLC" | costcntrl | float | € | FI |  |  |  | Client
| Electrical Installation | The cost for the installation of both power wiring to the system, and conttrols installation and wiring. | cstelcinst | float | € | FJ |  |  |  | Client
| Piping Diameter (IT Side) | The pipe size of the majority of the headers | pipitdia | int | mm | FK | BY |  |  | Client
| Piping Length (IT Side) | The total length of Heat Reuse piping on the IT side of the system | pipitlen | int | m | FL | BZ |  |  | Client
| Piping Insulation (IT Side) | Thickness of the pipe insulation | pipitins | int | mm | FM | CA |  |  | Client
| Cost of Piping on the IT side | The costs of installing the IT Cooling piping | costpipit | float | € | FN |  |  | (calculated) | Engine
| Piping Diameter (Heat Offtaker Side) | The pipe size of the majority of the headers | pipusdia | int | mm | FU | CB |  |  | Client
| Piping Length (Heat Offtaker Side) | The total length of Heat Reuse piping on the IT side of the system | pipuslen | int | m | FV | CC |  |  | Client
| Piping Insulation (Heat Offtaker Side) | thickness of the pipe insulation | pipusins | int | mm | FQ | CD |  |  | Client
| Cost of piping on the Offtaker Side, within Owner boundary | Cost to install the Offtaker piping, on Owner site | costpipusr | float | € | FR |  |  | (calculated) | Engine
| Valves and Fittings | An estimation of the ancillary piping devices | costvalit | float | € | FS |  |  | (calculated) | Engine
| Valves and Fittings | An estimation of the ancillary piping devices | costvalusr | float | € | FT |  |  | (calculated) | Engine
| Cost of Piping | The sum of all the piping installation costs | costpipe | float | € | FO | CE | = FN + FR + FS + FT | (calculated) | Engine
| Ancillary IT Facility Costs | Miscellaneous costs to accommodate the system | costanceq | float | € | FP | CG |  |  | Client
| Civil works associated | All cumulative costs to install the infrastructure, NOT within the Owner or Offtaker boundaries | costcvl | float | € | FW |  |  |  | Client
| Weight bearing elements | Facility structural costs | coststct | float | € | FX |  |  |  | Client
| The cost of installing the Heat Reuse System | Costs of installation, incurred at the Owners site | costinst | float | € | FY |  |  |  | Client
| What was the cost of the IT facility or data centre? | What is the reported value of the IT Facility? | costitctr | float | € | FZ | AI |  |  | Client
OWNER OPERATING COSTS | Space costs | The value of the real estate occupied by the heat reuse equipment | spaceval |  |  | GA |  |  |  | Client
| Energy usage for chillers | The cost of operating chillers, to replace the heat rejection of heat to the Offtaker | costchlr |  |  | GB |  |  |  | Client
| Energy usage for free-cooling | The cost of operating an alternate cooling strategy, to replace the heat rejection of heat to the Offtaker | costfrec |  |  | GC |  |  |  | Client
| Maintenance of the Heat Transfer System | Annual cost to maintain the system | costmaint |  |  | GD |  |  |  | Client
| incomplete |  | n |  |  | GE |  |  |  | Client
| incomplete |  | n |  |  | GF |  |  |  | Client
| incomplete |  | n |  |  | GG |  |  |  | Client
| incomplete |  | n |  |  | GH |  |  |  | Client
| incomplete |  | n |  |  | GI |  |  |  | Client
| incomplete |  | n |  |  | GJ |  |  |  | Client
| incomplete |  | n |  |  | GK |  |  |  | Client
| incomplete |  | n |  |  | GL |  |  |  | Client
| incomplete |  | n |  |  | GM |  |  |  | Client
| incomplete |  | n |  |  | GN |  |  |  | Client
| incomplete |  | n |  |  | GO |  |  |  | Client
| incomplete |  | n |  |  | GP |  |  |  | Client
| incomplete |  | n |  |  | GQ |  |  |  | Client
| incomplete |  | n |  |  | GR |  |  |  | Client
COMMON | Boundary definition |  | bounds | string | n/a | EG |  | HX Flanges | 500 CHAR | Client
| Discount Rate (for NPV = 0) |  | r | float | % | EH |  | 0.03 | 0.001 - 0.10 | Client
| incomplete |  | n |  |  | EI |  |  |  | Client
| Amortization time |  | T | float | years | EJ |  | 20 | .5 - 40.0 | Client
| incomplete |  | n |  |  | EK |  |  |  | Client
| incomplete |  | n |  |  | EL |  |  |  | Client
| incomplete |  | n |  |  | EM |  |  |  | Client
| incomplete |  | n |  |  | EN |  |  |  | Client
| incomplete |  | n |  |  | EO |  |  |  | Client
BOTTOM LINE | What was the cost to implement Heat Reuse? | The sum of all construction and project costs, before operations, by all parties, not including any offsets. | costproj | float | € | GS | AJ | (calculated) |  | Engine
| What will be the anticipated Operating Cost for one year? | Based on performance of the systems as rated, presuming fully loaded IT, and full heat utilization by the Offtaker system. | costoper | float | € | GT |  | (calculated) |  | Engine
| What is the sum of all direct incentives? | The sum of all rebates, bonuses, offsets, etc. | sumoffset | float | € | GU |  | (calculated) |  | Engine
| incomplete |  | n |  | € | GV |  | (calculated) |  | Engine
| incomplete |  | n |  | € | GW |  | (calculated) |  | Engine
| IRR |  | IRR | float | € | GX |  | (calculated) |  | Engine
| NPV |  | NPV | float | € | GY |  | (calculated) |  | Engine
| Net Return on Investment |  | ROI | float | € | GZ |  | (calculated) |  | Engine
| Net Economical Impact of this Heat Reuse System, for the first year? |  | impactyr | float | € | HA |  | (calculated) |  | Engine
| Net Economical Impact of this Heat Reuse System, for the Project Life? |  | impactlif | float | € | HB |  | (calculated) |  | Engine
EXTERNAL REFERENCES (there will be several more) | 125 Pipe By Length | THESE WILL BE THE CURRENT, ACTIVE PRICE per meter FOR PIPING, AT TIME OF CLIENT INPUT. WE WILL NEED TO CONFIRM ON WHICH PIPE STANDARD TO ANTICIPATE USAGE | pric125 | float | € | HC |  | (calculated) |  | External
| 140 Pipe By Length |  | pric140 | float | € | HD |  | (calculated) |  | External
| 160 Pipe By Length |  | pric160 | float | € | HE |  | (calculated) |  | External
| 180 Pipe By Length |  | pric180 | float | € | HF |  | (calculated) |  | External
| 200 Pipe By Length |  | pric200 | float | € | HG |  | (calculated) |  | External
| 225 Pipe By Length |  | pric225 | float | € | HH |  | (calculated) |  | External
| 250 Pipe By Length |  | pric250 | float | € | HI |  | (calculated) |  | External
| 280 Pipe By Length |  | pric280 | float | € | HJ |  | (calculated) |  | External
| 315 Pipe By Length |  | pric315 | float | € | HK |  | (calculated) |  | External
| 355 Pipe By Length |  | pric355 | float | € | HL |  | (calculated) |  | External
| 400 Pipe By Length |  | pric400 | float | € | HM |  | (calculated) |  | External
| 125 Valve Package |  | prval125 | float | € | HN |  | (calculated) |  | External
| 140 Valve Package |  | prval140 | float | € | HO |  | (calculated) |  | External
| 160 Valve Package |  | prval160 | float | € | HP |  | (calculated) |  | External
| 180 Valve Package |  | prval180 | float | € | HQ |  | (calculated) |  | External
| 200 Valve Package |  | prval200 | float | € | HR |  | (calculated) |  | External
| 225 Valve Package |  | prval225 | float | € | HS |  | (calculated) |  | External
| 250 Valve Package |  | prval250 | float | € | HT |  | (calculated) |  | External
| 280 Valve Package |  | prval280 | float | € | HU |  | (calculated) |  | External
| 315 Valve Package |  | prval315 | float | € | HV |  | (calculated) |  | External
| 355 Valve Package |  | prval355 | float | € | HW |  | (calculated) |  | External
| 400 Valve Package |  | prval400 | float | € | HX |  | (calculated) |  | External
HY
HZ
KU
KV
KW
KX
KY
KZ
CLIENT Fluctuation INPUT | Hourly Fluctuation Factor for Computing for 0:00 | The percentage of Computing normally availalble | dvrit00 | float | % | IA | ONLY SHOWN AT CLIENT DATA INPUT PAGE | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 1:00 | The percentage of Computing normally availalble | dvrit01 | float | % | IB |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 2:00 | The percentage of Computing normally availalble | dvrit02 | float | % | IC |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 3:00 | The percentage of Computing normally availalble | dvrit03 | float | % | ID |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 4:00 | The percentage of Computing normally availalble | dvrit04 | float | % | IE |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 5:00 | The percentage of Computing normally availalble | dvrit05 | float | % | IF |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 6:00 | The percentage of Computing normally availalble | dvrit06 | float | % | IG |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 7:00 | The percentage of Computing normally availalble | dvrit07 | float | % | IH |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 8:00 | The percentage of Computing normally availalble | dvrit08 | float | % | II |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 9:00 | The percentage of Computing normally availalble | dvrit09 | float | % | IJ |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 10:00 | The percentage of Computing normally availalble | dvrit10 | float | % | IK |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 11:00 | The percentage of Computing normally availalble | dvrit11 | float | % | IL |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 12:00 | The percentage of Computing normally availalble | dvrit12 | float | % | IM |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 13:00 | The percentage of Computing normally availalble | dvrit13 | float | % | IN |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 14:00 | The percentage of Computing normally availalble | dvrit14 | float | % | IO |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 15:00 | The percentage of Computing normally availalble | dvrit15 | float | % | IP |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 16:00 | The percentage of Computing normally availalble | dvrit16 | float | % | IQ |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 17:00 | The percentage of Computing normally availalble | dvrit17 | float | % | IR |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 18:00 | The percentage of Computing normally availalble | dvrit18 | float | % | IS |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 19:00 | The percentage of Computing normally availalble | dvrit19 | float | % | IT |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 20:00 | The percentage of Computing normally availalble | dvrit20 | float | % | IU |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 21:00 | The percentage of Computing normally availalble | dvrit21 | float | % | IV |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 22:00 | The percentage of Computing normally availalble | dvrit22 | float | % | IW |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Computing for 23:00 | The percentage of Computing normally availalble | dvrit23 | float | % | IX |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for January | The percentage of Computing normally availalble | dvritjan | float | % | IY |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for February | The percentage of Computing normally availalble | dvritfeb | float | % | IZ |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for March | The percentage of Computing normally availalble | dvritmar | float | % | JA |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for April | The percentage of Computing normally availalble | dvritapr | float | % | JB |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for May | The percentage of Computing normally availalble | dvritmay | float | % | JC |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for June | The percentage of Computing normally availalble | dvritjun | float | % | JD |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for July | The percentage of Computing normally availalble | dvritjul | float | % | JE |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for August | The percentage of Computing normally availalble | dvritaug | float | % | JF |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for September | The percentage of Computing normally availalble | dvritsep | float | % | JG |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for October | The percentage of Computing normally availalble | dvritoct | float | % | JH |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for November | The percentage of Computing normally availalble | dvritnov | float | % | JI |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Computing for December | The percentage of Computing normally availalble | dvritdec | float | % | JJ |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 0:00 | The percentage of heat used by Offtaker system | dvrusr00 | float | % | JK |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 1:00 | The percentage of heat used by Offtaker system | dvrusr01 | float | % | JL |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 2:00 | The percentage of heat used by Offtaker system | dvrusr02 | float | % | JM |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 3:00 | The percentage of heat used by Offtaker system | dvrusr03 | float | % | JN |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 4:00 | The percentage of heat used by Offtaker system | dvrusr04 | float | % | JO |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 5:00 | The percentage of heat used by Offtaker system | dvrusr05 | float | % | JP |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 6:00 | The percentage of heat used by Offtaker system | dvrusr06 | float | % | JQ |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 7:00 | The percentage of heat used by Offtaker system | dvrusr07 | float | % | JR |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 8:00 | The percentage of heat used by Offtaker system | dvrusr08 | float | % | JS |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 9:00 | The percentage of heat used by Offtaker system | dvrusr09 | float | % | JT |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 10:00 | The percentage of heat used by Offtaker system | dvrusr10 | float | % | JU |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 11:00 | The percentage of heat used by Offtaker system | dvrusr11 | float | % | JV |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 12:00 | The percentage of heat used by Offtaker system | dvrusr12 | float | % | JW |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 13:00 | The percentage of heat used by Offtaker system | dvrusr13 | float | % | JX |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 14:00 | The percentage of heat used by Offtaker system | dvrusr14 | float | % | JY |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 15:00 | The percentage of heat used by Offtaker system | dvrusr15 | float | % | JZ |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 16:00 | The percentage of heat used by Offtaker system | dvrusr16 | float | % | KA |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 17:00 | The percentage of heat used by Offtaker system | dvrusr17 | float | % | KB |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 18:00 | The percentage of heat used by Offtaker system | dvrusr18 | float | % | KC |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 19:00 | The percentage of heat used by Offtaker system | dvrusr19 | float | % | KD |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 20:00 | The percentage of heat used by Offtaker system | dvrusr20 | float | % | KE |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 21:00 | The percentage of heat used by Offtaker system | dvrusr21 | float | % | KF |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 22:00 | The percentage of heat used by Offtaker system | dvrusr22 | float | % | KG |  | 100% | 0 - 100% | Client
| Hourly Fluctuation Factor for Heat Use for 23:00 | The percentage of heat used by Offtaker system | dvrusr23 | float | % | KH |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for January | The percentage of heat used by Offtaker system | dvrusrjan | float | % | KI |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for February | The percentage of heat used by Offtaker system | dvrusrfab | float | % | KJ |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for March | The percentage of heat used by Offtaker system | dvrusrmar | float | % | KK |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for April | The percentage of heat used by Offtaker system | dvrusrapr | float | % | KL |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for May | The percentage of heat used by Offtaker system | dvrusrmay | float | % | KM |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for June | The percentage of heat used by Offtaker system | dvrusrjun | float | % | KN |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for July | The percentage of heat used by Offtaker system | dvrusrjul | float | % | KO |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for August | The percentage of heat used by Offtaker system | dvrusraug | float | % | KP |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for September | The percentage of heat used by Offtaker system | dvrusrsep | float | % | KQ |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for October | The percentage of heat used by Offtaker system | dvrusroct | float | % | KR |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for November | The percentage of heat used by Offtaker system | dvrusrnov | float | % | KS |  | 100% | 0 - 100% | Client
| Monthly Fluctuation Factor for Heat Use for December | The percentage of heat used by Offtaker system | dvrusrdec | float | % | KT |  | 100% | 0 - 100% | Client
Degrees

## Methods
We are assisting planners in developing new projects, and will offer them tools. How will we help them calculate the profitability of a Heat Reuse Project?
Assisting planners in evaluating the profitability of a Heat Reuse Project involves providing tools and methodologies for analyzing both the costs and revenues associated with such initiatives. The profitability analysis should encompass initial investment costs, operational costs, savings, and potential revenue streams from the sale or use of recovered heat. Here's how you can help planners calculate the profitability:
1. Initial Investment Costs
Infrastructure Costs: Costs associated with retrofitting existing systems or installing new heat recovery and transfer equipment.
Design and Engineering Costs: Expenses for professional services including feasibility studies, engineering design, and project management.
2. Operational Costs
Maintenance Costs: Regular maintenance of heat recovery systems and associated infrastructure.
Energy Costs: Additional energy required to operate the heat recovery system, if applicable.
Other Operational Expenses: Costs such as insurance, taxes, and permits related to the heat reuse system.
3. Savings
Energy Savings: Reduced energy costs from using recovered heat for heating buildings, water, or industrial processes within the data center or in neighboring facilities.
Incentives: Government or utility incentives, grants, or tax breaks for implementing energy efficiency or renewable energy projects.
4. Revenue Streams
Sale of Excess Heat: Income from selling recovered heat to external parties, such as district heating systems or nearby industrial users.
Carbon Credits: Revenue from carbon offset markets if the project reduces greenhouse gas emissions.
Tools and Methodologies for Calculation
Economic Models
Net Present Value (NPV): Calculates the present value of net cash flows (revenues and savings minus costs) over the project's lifetime, discounting future cash flows to account for the time value of money.
Internal Rate of Return (IRR): Determines the discount rate at which the NPV of all cash flows (both positive and negative) from a project equals zero, effectively measuring the project's profitability.
Payback Period: Estimates the time required for the project to recoup its initial investment costs through savings and revenues.
Heat Reuse Specific Tools
To calculate the Net Present Value (NPV) of a Heat Reuse Project for a client, you'll need detailed information about the project's cash flows over its expected life. This includes both the initial investment costs and the ongoing operational costs and revenues. Here's a breakdown of the specific information needed from the client:
Initial Investment Costs
Capital Expenditure (CapEx): The total upfront costs needed for the project, including purchasing equipment, installation, and any modifications to existing infrastructure.
Design and Engineering Costs: Costs associated with planning, designing, and engineering the heat reuse system.
Operational Costs
Maintenance and Repair Costs: Estimates of the costs for maintaining and repairing the heat reuse system over its lifetime.
Operational Expenditure (OpEx): Ongoing costs to operate the system, which may include additional energy costs, labor, and any materials needed for operation.
Revenue and Savings
Energy Savings: Estimated savings from using the recovered heat, which could reduce the need for purchased energy.
Revenue from Heat Sales: If applicable, projected income from selling excess heat to third parties.
Incentives and Subsidies: Information on any government or utility incentives, subsidies, or tax credits that the project will qualify for.
Project Life and Discount Rate
Expected Project Lifetime: The anticipated operational lifespan of the heat reuse system, which impacts the calculation of cash flows over time.
Discount Rate: The rate used to discount future cash flows back to their present value. This could be the client's cost of capital or a rate that reflects the risk profile of the project.
Additional Information
Escalation Rates: Expected annual increases in energy prices, operational costs, and revenues, which will affect future cash flows.
Residual Value: If the project or its components have a salvage value at the end of the expected life, this should be included in the calculations.
Tax Implications: Information on how taxes might impact the project's cash flows, including depreciation and any tax credits.
Collecting detailed and accurate information in these areas is crucial for performing a comprehensive NPV analysis. This analysis will help the client understand the financial viability of the heat reuse project by comparing the present value of its projected net cash flows (revenues and savings minus costs) against the initial investment. A positive NPV indicates that the project is expected to generate value over its lifetime, making it a potentially worthwhile investment.
NPV = Net Present Value
Rt = net revenue (or savings) in period t
Ct. = net cost (or investment) in period t
R. = discount rate
T. = time period (year)
C0​ = initial investment costs
Now, I'll ask for the inputs one by one:
Initial Investment Costs (C0​): What is the total initial investment cost for the Heat Reuse Project?
Discount Rate (r): What discount rate should we use to discount future cash flows back to their present value?
Project Lifetime: Over how many years are we expecting to analyze the project?
For each year of the project, I will then ask for:
Annual Operational Costs (Ct​): What are the expected operational costs for each year?
Annual Revenue and Savings (Rt​): What is the expected revenue (from heat sales, etc.) and savings (in energy costs, etc.) for each year?
Please provide the initial investment cost and discount rate to start with.
C0 = 1000000; r = 3.5%
Great, you've provided the following inputs:
Initial Investment Costs (C0C0​) = $1,000,000
Discount Rate (rr) = 3.5%
Next, could you please provide the expected lifetime of the project in years?
20
Thank you for providing the project's expected lifetime. With a 20-year analysis period, we'll now need the annual operational costs and the annual revenue and savings for each year of the project.
Starting with Year 1 and moving through Year 20, for each year please provide:
Annual Operational Costs (CtCt​): The expected operational costs.
Annual Revenue and Savings (RtRt​): The expected revenue from heat sales and savings in energy costs.
If the costs and revenues are expected to grow at a constant rate annually, you can provide the values for the first year and the growth rate instead of year-by-year details. Otherwise, we'll need the year-by-year details.
Could you please provide the details for Year 1, or if applicable, the growth rate for costs and revenues?
Ct = 50,000 , grow 3% per year;
Thank you for the operational costs details:
Year 1 Annual Operational Costs (CtCt​) = $50,000
Operational Costs Growth Rate = 3% per year
Next, we need the equivalent information for the annual revenue and savings:
Year 1 Annual Revenue and Savings (RtRt​): What are the expected revenue from heat sales and savings in energy costs for the first year?
Revenue and Savings Growth Rate: If the revenue and savings are expected to grow at a constant rate annually, please provide that growth rate.
Could you please provide these details for the annual revenue and savings?
Rt = $50,000, growth = 3% per year
It seems there was a misunderstanding in the calculation, particularly in not correctly applying the growth rates to differentiate between the costs and revenues over the project's lifetime. Given the inputs provided were identical for both costs and revenues with the same growth rates, the net cash flow for each year would theoretically be zero, assuming costs and revenues cancel each other out exactly. This simplistic scenario led to an incorrect NPV calculation.
Let's correct the approach by ensuring that we're accurately accounting for the initial investment and then applying the growth rates to both costs and revenues separately to reflect the actual net cash flow each year.
Given that both costs and revenues start at $50,000 and grow at a rate of 3% per year, in a simplified model where they grow at the same rate and start from the same base, the operational net cash flow (revenue minus costs) would be zero each year, not contributing to the NPV aside from the initial investment. This overlooks the initial investment recovery through these operations, suggesting a potential mistake in the conceptual approach or an oversight in the provided data.
To proceed accurately, we need to ensure we're considering all relevant factors, including any additional benefits, savings, or potential discrepancies between cost and revenue growth. If the intention was to reflect a scenario where operational efficiencies or additional revenues (not covered in the initial inputs) play a role, we should adjust the model accordingly.
For a meaningful NPV calculation, the revenue and savings should typically exceed operational costs, or there should be significant upfront savings or revenue opportunities not captured in the initial simplified model.
Could you clarify if there are additional factors or corrections to the inputs provided? This could include higher initial revenues, different growth rates, or additional benefits not yet accounted for. ​​
Corrected Rt = 100,000, growth = 3.5%
With the corrected annual revenue and savings starting at $100,000 and growing at a rate of 3.5% per year, the Net Present Value (NPV) of the Heat Reuse Project over a 20-year period, with an initial investment of $1,000,000 and a discount rate of 3.5%, is approximately $9,266.05.
This positive NPV indicates that, according to the corrected inputs, the project is expected to generate a value over its lifetime that exceeds the initial investment when accounting for the time value of money. This suggests the Heat Reuse Project could be a financially viable option for the client. ​​

## Clarifications
Clarifications and Definitions Page | THIS PAGE IS IN EARLY DEVELOPMENT
On this Excel workbook tab, we will add unstructured information regarding explanations, clarifiactions and definitions of various issues, perhaps including definitions of specific data points and how they are used or derived. There will be a SEPARATE PAGE FOR INSTRUCTIONS ON HOW TO USE THIS TOOL.
Heat Reuse Effectiveness (HRE) is a metric used to quantify the efficiency of heat recovery and reuse from a system, such as a data center. It measures the proportion of waste heat that is successfully captured and reused in comparison to the total potential heat that could be reused. The HRE is crucial for evaluating the sustainability and energy efficiency of facilities, especially those generating significant amounts of excess heat.
To calculate the Heat Reuse Effectiveness, you can use the following formula:
HRE = Useful Heat Reused / Total Waste Heat Available. HRE == ERE
Where:
Useful Heat Reused is the amount of heat captured from the data center and successfully used for another purpose, such as heating buildings, domestic hot water production, or industrial processes. It is measured in energy units over a specific time period (e.g., megawatt-hours per year).
Total Waste Heat Available is the total amount of excess heat produced by the data center that could potentially be reused. This is also measured in the same energy units over the same time period.
The HRE value is typically expressed as a percentage. A higher HRE indicates a more efficient use of waste heat, signifying a more sustainable and energy-efficient operation. For example, an HRE of 75% means that 75% of the data center's waste heat has been successfully reused.
To effectively calculate HRE, data center operators need to:
Quantify the Total Waste Heat Available: This involves measuring or estimating the total heat output from the data center's equipment, including servers, storage, and networking gear. This can be challenging, as it requires comprehensive data on the energy consumption and heat production of each component.
Measure the Useful Heat Reused: This step requires tracking the amount of waste heat that is captured and utilized effectively. It involves monitoring the systems that transfer and use the heat, such as heat exchangers and the infrastructure for the applications benefiting from the heat reuse.
Implementing systems for accurately measuring these quantities is essential for calculating HRE and can involve a mix of direct measurement, estimation, and modeling based on the data center's operational parameters and the configuration of the heat reuse systems.
The Heat Reuse Factor (HRF) is another important metric for assessing the sustainability and efficiency of data centers, especially in terms of how effectively they can repurpose their waste heat for beneficial uses. Unlike Heat Reuse Effectiveness (HRE), which focuses on the proportion of heat reused out of the total waste heat available, HRF typically provides insight into how much of the data center's energy consumption is offset by the reuse of its waste heat.
The calculation of HRF can vary based on the specific definition and application, but a common formula to calculate Heat Reuse Factor is:
HRF = Energy Reused for Beneficial Purposes / Total Energy Input to the Data Center;
HRF​ == ERF
Where:
Energy Reused for Beneficial Purposes is the amount of energy (in energy units like megawatt-hours, MWh) that is captured from the data center’s waste heat and successfully utilized for other applications. These applications could range from heating buildings to supplying district heating networks or industrial processes.
Total Energy Input to the Data Center refers to the total amount of energy consumed by the data center, including all IT equipment, cooling systems, and other infrastructure. This is also measured in the same energy units.
The HRF is typically expressed as a dimensionless ratio or percentage. A higher HRF indicates a greater proportion of the data center's energy input is being effectively reused, enhancing its overall energy efficiency and reducing its environmental impact.
Steps to Calculate HRF:
Quantify the Energy Reused for Beneficial Purposes: Measure or estimate the amount of waste heat from the data center that is captured and converted into useful energy for other applications. This may require detailed monitoring of heat recovery systems and their output.
Determine the Total Energy Input to the Data Center: This involves calculating the total energy consumption of the data center, including IT equipment, cooling, lighting, and other infrastructure over the same period.
Calculate the HRF: Use the formula above to compute the HRF by dividing the energy reused by the total energy input to the data center.
Considerations:
Accurate measurement or estimation of both the energy reused and the total energy input is crucial for a reliable HRF calculation.
The HRF provides valuable insight into the data center's efficiency and environmental impact, helping to identify opportunities for improvement and showcasing the benefits of heat recovery initiatives.
In addition to HRF, it's beneficial to consider other sustainability metrics like PUE (Power Usage Effectiveness) and HRE to get a comprehensive view of a data center's performance.
INDUSTRY ORGANIZATIONS
The concept of heat reuse and energy reuse from data centers and other industrial operations is growing in interest across various sectors, with several professional and industry organizations actively involved or showing interest. These organizations play crucial roles in setting standards, conducting research, sharing best practices, and advocating for policies that promote the efficient use of energy. Here are some of the key organizations involved in heat reuse or energy reuse:
The Green Grid - This organization is focused on improving energy efficiency in data centers and business computing ecosystems. It provides a forum for IT industry and data center professionals to share information and best practices for improving energy efficiency.
ASHRAE (American Society of Heating, Refrigerating and Air-Conditioning Engineers) - ASHRAE is heavily involved in creating standards and guidelines for building systems, including those for data centers. They have committees and publications dedicated to energy efficiency and the reuse of heat.
International Energy Agency (IEA) - While not solely focused on heat reuse, the IEA conducts significant research and policy advocacy on energy efficiency and sustainability. They often publish reports and guidelines that include best practices for energy reuse in various sectors.
Uptime Institute - Known for its focus on improving the performance, efficiency, and reliability of data centers, the Uptime Institute addresses issues around energy use and has shown interest in sustainable practices, including heat reuse.
Data Center Alliance - This broad organization includes members from various sectors of the data center industry. Sustainability and energy efficiency are key topics, with some focus on heat reuse as part of a broader interest in green data center practices.
CIBSE (Chartered Institution of Building Services Engineers) - Based in the UK, CIBSE provides guidance and standards for building services engineering, including the efficient design and operation of buildings for energy use. They have resources and special interest groups focused on energy efficiency and sustainability.
ISO (International Organization for Standardization) - ISO develops and publishes international standards, including those related to energy management systems (e.g., ISO 50001) which can encompass heat and energy reuse strategies.
The Carbon Trust - An organization focused on helping businesses, governments, and the public sector to accelerate the move to a sustainable, low carbon economy. They provide advice and solutions for reducing carbon emissions and energy use, which can include strategies for heat and energy reuse.
These organizations, among others, are actively contributing to the development, implementation, and promotion of heat and energy reuse technologies and practices. They provide a wealth of resources for businesses and professionals looking to adopt more sustainable energy practices, including standards, best practices, research findings, and forums for collaboration.
The Open Compute Project (OCP) is a key player in the push towards more efficient and sustainable data center operations, including the area of heat reuse. The OCP's active involvement in heat reuse can be seen through its dedicated workgroup that focuses on several critical aspects:
Heat Reuse Policy: This area of focus aims to address and influence regulatory, policy, and standards-related matters that impact the ability of organizations to implement heat reuse solutions. By engaging with policy makers and stakeholders, the OCP seeks to create a favorable environment for the adoption of heat reuse practices.
Heat Reuse Reference Design: Here, the OCP is working to develop and disseminate best practices and design principles for heat reuse in data centers. This includes providing guidelines, case studies, and reference designs that can help organizations understand how to integrate heat reuse into their operations effectively and efficiently.
Heat Reuse Economics: Understanding the economic implications and benefits of heat reuse is crucial for its adoption. The OCP's focus on the economics of heat reuse involves analyzing cost-benefit aspects, identifying financial incentives, and making the business case for investing in heat reuse technologies and projects.
The Open Compute Project's efforts in these three areas are essential for advancing the adoption of heat reuse technologies in data centers and related industries. By addressing policy, design, and economic factors, the OCP is helping to pave the way for broader implementation of sustainable and efficient energy practices. This involvement should be recognized and leveraged by industry professionals, policymakers, and stakeholders interested in promoting and benefiting from heat reuse solutions.

## NREL Metrics
https://drive.google.com/file/d/1W6hG85K4Oc6wiIk-MxPiFbGH9Q5tVp2N/edit?pli=1

## STOCHASTIC Data Table
index | name | Client | source | date1 | date2 | city | state | country | sitelat | sitelong | userlat | userlong | siteowner | soweblink | ituser | warea | rack | rackkw | itweblink | huowner | howeblink | hruser | huweblink | usertype | relationship | date3 | product | sitepwr | itpwr | pwrsce1 | pwrtype1 | pwrrate1 | pwrrate1ad | pwr1prop | pwrsce2 | pwrtype2 | pwrrate2 | pwrrate2ad | pwrrate2prop | pwralt | pwralttype | pwrratealt | pwrratealtad | h2ouse | h2orate | usebldg | usecamp | useprem | usedist | ere | erf | hre | hrf | hrec | hrfc | wha | uhr | uhrdvrad | hredvrad | pwrf1 | T1min | T1max | T1 | T2min | T2max | T2 | itdt | fluid1 | P2 | P1 | dpit | F1 | fluid1vis | fluid1hc | gwp1 | odp1 | T4min | T4max | T4 | T3min | T3max | T3 | userdt | fluid2 | P4 | P3 | F2 | boost | fluid2vis | fluid2hc | storst | storstsz | storsttyp | storlt | storltsz | dpuser | storlttyp | boosteqp | bsthpcop | bstblreff | pwrf2 | dvrusrday | dvrusryr | datasize | itaircl | itdrcl | itchipcl | itpltcl | it1imm | it2imm | itdivrday | itdvryr | whadvr | n | n | prod1 | prod1rev | prod2 | prod2rev | althtrate | usrpwrrate | benusrcard | benusrmisc | benusremit | benusrnrg | cstusrmnt | cstustext | cstusrsto | cstushteq | n | benitcool | cstitcool | n | n | n | bounds | r | n | T | n | n | n | n | n | avdemit | avdh20 | heatrev | nrgcerts | avdeqpt | subs | avdemtcst | avdtax | n | n | n | costplan | costperm | costarch | costeng | n | costmjeq | costmneq | cstinslpip | costcntrl | cstelcinst | pipitdia | pipitlen | pipitins | costpipit | costpipe | costanceq | pipusins | costpipusr | costvalit | costvalusr | pipusdia | pipuslen | costcvl | coststct | costinst | costitctr | spaceval | costchlr | costfrec | costmaint | n | n | n | n | n | n | n | n | n | n | n | n | n | n | costproj | costoper | sumoffset | n | n | IRR | NPV | ROI | impactyr | impactlif | pric125 | pric140 | pric160 | pric180 | pric200 | pric225 | pric250 | pric280 | pric315 | pric355 | pric400 | prval125 | prval140 | prval160 | prval180 | prval200 | prval225 | prval250 | prval280 | prval315 | prval355 | prval400 | n | n | dvrit00 | dvrit01 | dvrit02 | dvrit03 | dvrit04 | dvrit05 | dvrit06 | dvrit07 | dvrit08 | dvrit09 | dvrit10 | dvrit11 | dvrit12 | dvrit13 | dvrit14 | dvrit15 | dvrit16 | dvrit17 | dvrit18 | dvrit19 | dvrit20 | dvrit21 | dvrit22 | dvrit23 | dvritjan | dvritfeb | dvritmar | dvritapr | dvritmay | dvritjun | dvritjul | dvritaug | dvritsep | dvritoct | dvritnov | dvritdec | dvrusr00 | dvrusr01 | dvrusr02 | dvrusr03 | dvrusr04 | dvrusr05 | dvrusr06 | dvrusr07 | dvrusr08 | dvrusr09 | dvrusr10 | dvrusr11 | dvrusr12 | dvrusr13 | dvrusr14 | dvrusr15 | dvrusr16 | dvrusr17 | dvrusr18 | dvrusr19 | dvrusr20 | dvrusr21 | dvrusr22 | dvrusr23 | dvrusrjan | dvrusrfab | dvrusrmar | dvrusrapr | dvrusrmay | dvrusrjun | dvrusrjul | dvrusraug | dvrusrsep | dvrusroct | dvrusrnov | dvrusrdec
0 | Little Hall | Stochastic | Client | 2024-03-02 | 2024-03-02 | Carraga San Georgio | Padova | IT | 45.3231 | 11.7738 | 45.3346 | 11.7858 | Saint Anthony |  | Tony's Data Works |  |  |  |  | Hotel Esplanade Tergesteo |  | Hotel Esplanade Tergesteo |  | Spa Heating | Seller/buyer | 2021-03-25 | [22 empty] | 1625 |  |  | 0.875 |  |  |  | 557.4495 | 487.7683 | 487.7683 | 487.7683 |  |  |  | 38 |  |  | 30 | 8 | Water |  |  |  | 1000 | [6 empty] | 25 |  |  | 35 | 10 | Water |  |  | 700 | [14 empty] | 100% | 100% | [7 empty] | 100% | 100% | [121 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
1 | Big Hall | Stochastic | Client | 2024-03-03 | 2024-03-03 | Jumeirah | Dubai | UAE | 25.0987 | 55.1602 |  |  | Al Falak Innovations |  | Al Falak Innovations |  |  |  |  | Atlantis Hotel |  | Atlantis Hotel |  | Utilities | Seller/buyer | 2022-07-23 | [22 empty] | 5625 |  |  | 0.79333 |  |  |  | 10452.178 | 8292.0612 | 8292.0612 | 8292.0612 |  |  |  | 50 |  |  | 35 | 15 | Water |  |  |  | 10000 | [6 empty] | 30 |  |  | 47 | 17 | Water |  |  | 7000 | [14 empty] | 100% | 100% | [7 empty] | 100% | 100% | [121 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
2 | Data Farm | Stochastic | Client | 2024-03-04 | 2024-03-04 | Marthasville | MO | USA | -91.1017 | 38.6346 |  |  | Uncle Jack |  | Amazing AI |  |  |  |  | Hopewell Fish Farm |  | Hopewell Fish Farm |  | Aquaculatural | Seller/buyer | 2022-01-05 | Fish | [21 empty] | 100 |  |  | 0.57692 |  |  |  | 1811.7109 | 1045.2178 | 749.0728 | 749.0728 |  |  |  | 40 |  |  | 27 | 13 | Water |  |  |  | 2000 | [6 empty] | 25 |  |  | 35 | 10 | Water |  |  | 1500 | [14 empty] | 100% | 71.67% | [7 empty] | 100% | 100% | [121 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 45% | 0% | 0% | 15% | 100% | 100% | 100%
3 | Data Ranch | Stochastic | Client | 2024-03-05 | 2024-03-05 | Lipica |  | Slovenia | 45.6665 | 13.8713 | 45.6663 | 13.8817 | Confidential |  | Jak Se Mas |  |  |  |  | Kobilarna Stables |  | Kobilarna Stables |  | Agriculatural | Benefactor | 2024-02-02 | [22 empty] | 816 |  |  | 0.79333 |  |  |  | 5226.089 | 4146.0306 | 3005.8722 | 3005.8722 |  |  |  | 40 |  |  | 25 | 15 | Water |  |  |  | 5000 | [6 empty] | 20 |  |  | 37 | 17 | Water |  |  | 3500 | [14 empty] | 100% | 72.5% | [7 empty] | 100% | 100% | [121 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 45% | 0% | 0% | 25% | 100% | 100% | 100%
4 | Data Town | Stochastic | Client | 2024-03-06 | 2024-03-06 | Edinburough |  | UK | 56 | -2.8 | 55.9362 | -3.0652 | Haddington |  | Haddington Sports Association |  |  |  |  | Newcraighall |  | Newcragihall Public Park |  | Public Space Heating | Benefactor | 2020-03-03 | [22 empty] | 19725 |  |  | 0.81818 |  |  |  | 3065.9722 | 2508.5227 | 1609.6354 | 1609.6354 |  |  |  | 40 |  |  | 29 | 11 | Water |  |  |  | 4000 | [6 empty] | 25 |  |  | 37 | 12 | Water |  |  | 3000 | [14 empty] | 87.5% | 73.33% | [7 empty] | 100% | 100% | [121 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 45% | 0% | 0% | 35% | 100% | 100% | 100%
5
n | n/a | Client | Client | 2023-12-31 | 2023-12-31 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | = siteowner | n/a | n/a | n/a | n/a | n/a | n/a | =huowner | n/a | SELECTION BOX: | n/a | 2023-12-31 | No | n/a | n/a | n/a | n/a | n/a | n/a | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0 | 0 | No | Yes | Yes | 0 |  |  | (calculated) | (calculated) |  |  | (calculated) | (calculated) | (calculated) | (calculated) | 25 | 10 | 40 | 30 | 20 | 60 | 40 | (calculated) | Water | 4.0 | 1.0 | (calculated) |  | n/a | n/a | n/a | n/a | 20 | 40 | 25 | 30 | 50 | 45 | (calculated) | Water | 5 | 3 |  | No |  |  | No |  | Tank | No |  | (calculated) | Reservior | Heat Pump |  |  | 25 | 1 | 1 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 1 | 1 | =wha |  |  | No | 0 | No | 0 | [15 empty] | HX Flanges | 0.03 |  | 20 | [30 empty] | = FN + FR + FS + FT | [29 empty] | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) |  | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) | (calculated) |  |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Identifier for each unique Record | The "Common" name for the site | Regardless of existing or new record, the common name for "where did it come from" | Source that the data was gathered from | Date of entry of the data | Date of last update of the data | Nearest City to the site location | State or region of the site location | Country of the location | Geographical Latitude of the site | Geographical Longitude of the site | Geographical Latitude of the heat user | Geographical Longitude of the heat user | Principal owner of the Data Facility | Any online information regarding site owners | Principal tenant or user of the site | Footprint area of the white space | The number of data cabinets of racks | The avaerage amount of power per standard rack | Any online information regarding tenants or users of the data centre | Principal owner of the Heat User System | Any online information regarding the owner/operator of the heat user system | Principal user of the heat | Any online information regarding the actual user(s) of the heat | General category of heat user | Short explanation of the relationship between the It Facility and the Heat User |  | What does the Heat User get from the use of the heat, if there is an "industrial" user? | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | When User is off-premises, how far to the first User | Use these figures if offered by Client | Use these figures if offered by Client | Use these figures if calculated within our engine | Use these figures if calculated within our engine | Use these figures if offered by Client | Use these figures if offered by Client | Heat made available from the IT System | Heat actually processed by User system | Total Heat multiplied by both diversity factors | Hre, adjusted by all four factors | Mostly, will be the pump power | 0 | 0 | 38 | 0 | 0 | 30 | 8 | What is the medium being used for capturing heat from the IT system? | Gauge Pressure at the Heat Exchanger | Gauge Pressure at the Heat Exchanger | Heat Exchanger "Delta P", on the IT Side | Fluid flow of IT Cooling Medium | Viscosity of IT Cooing Medium | Heat Capacity of IT Cooling Medium | GWP of IT Cooling Medium | ODP of IT Cooling Medium | 0 | 0 | 25 | 0 | 0 | 35 | 10 | What is the medium being used for heating? | Gauge Pressure at the Heat Exchanger | Gauge Pressure at the Heat Exchanger | What is the fluid flow in the User side? | If the User side fluid is not suffiently warm enough for the User's benefit, how is it further heated? | What is the viscosity of the fluid on the User side? | What is the Heat Capacity of the User side fluid? | If there is some kind of buffer tank? | How much fluid is stored or buffered? | What type of storage is there? | If there is a reservior or large body of water? | What is the volume of the large, long term storage? | Heat Exchanger "Delta P", on the User Side | What type of storage is there? | What is used to make the temperature "usable"? | IF a heat pump is used, how efficient is that heat pump? | IF a boiler is used, how efficient is that boiler? | Power for fluid movment on the Hat User side | Calculated from Client Input, DAILY swing in Usage | Calculated from Client Input, ANNUAL swing in Usage | What is the size of the computing equipment, in "Computing Terms" | How much of the IT Equipment is Cooled by Air ("traditional") (%) | How much of the IT Equipment is Cooled by Rack Door Heat Exchanger (%) | How much of the IT Equipment is Cooled by "Direct-to-Chip" Cold Plate (%) | How much of the IT Equipment is Cooled by "Other" Cold Plate (%) | How much of the IT Equipment is Cooled by Single Phase Immersion (%) | How much of the IT Equipment is Cooled by Two Phase Immersion (%) | Daily swing in available heat, from Client input | Annual swing in available heat, from Client input | Total Waste Hat Available, multiplied by both diversity factors |  |  | Is there an industrial use for the heat? If so, what is the primary product? | Annual revenue to User from Product 1 | Is there an industrial use for the heat? If so, what is the secondary product? | Annual revenue to User from Product 2 | What would heat cost RATE if there were no reuse? | Cost of electricity (User) | Carbon Benefits | Other Benefits | Emissions avoided at the Heat User | Energy savings certificates (or equivalent) For User | User Cost of Maintenance | External User equipment costs | Costs of Storage Equipment | Ancillary Heat User Equipment Costs | incomplete | Advanced Cooling Capacity | Cost of cooling energy (IT facility) | incomplete |  | incomplete | Boundary definition | Discount Rate (for NPV = 0) | incomplete | Amortization time | incomplete | incomplete | incomplete | incomplete | incomplete | Emissions Avoided at the IT facility | Water Usage Avoidance | Earnings from selling the heat | Energy savings certificates (or equivalent) IT facility | Savings Associated to Avoided Equipment | Subsidies | Emissions Costs Avoided | Tax rebates | incomplete | incomplete | incomplete | Costs associated with the development of the project | Costs associated with securing permits, and complying with any jurisdictional regulations | Costs of engaging architects as required | Costs of engaging engineers as required | incomplete | Costs for the major equipment of Heat Reuse | Ancillary Equipment at Owner space | the costs of installing the major equipment within the Owners site, exclusice of piping. | The sum of all electronic monitoring and controlling devices, including one local "PLC" | The cost for the installation of both power wiring to the system, and conttrols installation and wiring. | The pipe size of the majority of the headers | The total length of Heat Reuse piping on the IT side of the system | Thickness of the pipe insulation | The costs of installing the IT Cooling piping | The sum of all the piping installation costs | Miscellaneous costs to accommodate the system | thickness of the pipe insulation | Cost to install the User piping, on Owner site | An estimation of the ancillary piping devices | An estimation of the ancillary piping devices | The pipe size of the majority of the headers | The total length of Heat Reuse piping on the IT side of the system | All cumulative costs to install the infrastructure, NOT within the Owner or User boundaries | Facility structural costs | Costs of installation, incurred at the Owners site | What is the reported value of the IT Facility? | The value of the real estate occupied by the heat reuse equipment | The cost of operating chillers, to replace the heat rejection of heat to the User | The cost of operating an alternate cooling strategy, to replace the heat rejection of heat to the User | Annual cost to maintain the system | incomplete | incomplete | incomplete | incomplete | incomplete | incomplete | incomplete | incomplete | incomplete | incomplete | incomplete | incomplete | incomplete | incomplete | The sum of all construction and project costs, before operations, by all parties, not including any offsets. | Based on performance of the systems as rated, presuming fully loaded IT, and full heat utilization by the User system. | The sum of all rebates, bonuses, offsets, etc. | incomplete | incomplete | IRR | NPV | Net Return on Investment | Net Economical Impact of this Heat Reuse System, for the first year? | Net Economical Impact of this Heat Reuse System, for the Project Life? | 125 Pipe By Length | 140 Pipe By Length | 160 Pipe By Length | 180 Pipe By Length | 200 Pipe By Length | 225 Pipe By Length | 250 Pipe By Length | 280 Pipe By Length | 315 Pipe By Length | 355 Pipe By Length | 400 Pipe By Length | 125 Valve Package | 140 Valve Package | 160 Valve Package | 180 Valve Package | 200 Valve Package | 225 Valve Package | 250 Valve Package | 280 Valve Package | 315 Valve Package | 355 Valve Package | 400 Valve Package |  |  | The percentage of Computing normally availalble 00:00 | The percentage of Computing normally availalble 01:00 | The percentage of Computing normally availalble 02:00 | The percentage of Computing normally availalble 03:00 | The percentage of Computing normally availalble 04:00 | The percentage of Computing normally availalble 05:00 | The percentage of Computing normally availalble 06:00 | The percentage of Computing normally availalble 07:00 | The percentage of Computing normally availalble 08:00 | The percentage of Computing normally availalble 09:00 | The percentage of Computing normally availalble 10:00 | The percentage of Computing normally availalble 11:00 | The percentage of Computing normally availalble 12:00 | The percentage of Computing normally availalble 13:00 | The percentage of Computing normally availalble 14:00 | The percentage of Computing normally availalble 15:00 | The percentage of Computing normally availalble 16:00 | The percentage of Computing normally availalble 17:00 | The percentage of Computing normally availalble 18:00 | The percentage of Computing normally availalble 19:00 | The percentage of Computing normally availalble 20:00 | The percentage of Computing normally availalble 21:00 | The percentage of Computing normally availalble 22:00 | The percentage of Computing normally availalble 23:00 | The percentage of Computing normally availalble January | The percentage of Computing normally availalble February | The percentage of Computing normally availalble March | The percentage of Computing normally availalble April | The percentage of Computing normally availalble May | The percentage of Computing normally availalble June | The percentage of Computing normally availalble July | The percentage of Computing normally availalble August | The percentage of Computing normally availalble September | The percentage of Computing normally availalble October | The percentage of Computing normally availalble November | The percentage of Computing normally availalble December | The percentage of heat used by User system 0:00 | The percentage of heat used by User system 01:00 | The percentage of heat used by User system 02:00 | The percentage of heat used by User system 03:00 | The percentage of heat used by User system 04:00 | The percentage of heat used by User system 05:00 | The percentage of heat used by User system 06:00 | The percentage of heat used by User system 07:00 | The percentage of heat used by User system 08:00 | The percentage of heat used by User system 09:00 | The percentage of heat used by User system 10:00 | The percentage of heat used by User system 11:00 | The percentage of heat used by User system 12:00 | The percentage of heat used by User system 13:00 | The percentage of heat used by User system 14:00 | The percentage of heat used by User system 15:00 | The percentage of heat used by User system 16"00 | The percentage of heat used by User system 17:00 | The percentage of heat used by User system 18:00 | The percentage of heat used by User system 19:00 | The percentage of heat used by User system 20:00 | The percentage of heat used by User system 21:00 | The percentage of heat used by User system 22:00 | The percentage of heat used by User system 23:00 | The percentage of heat used by User system January | The percentage of heat used by User system February | The percentage of heat used by User system March | The percentage of heat used by User system April | The percentage of heat used by User system May | The percentage of heat used by User system June | The percentage of heat used by User system July | The percentage of heat used by User system August | The percentage of heat used by User system September | The percentage of heat used by User system October | The percentage of heat used by User system November | The percentage of heat used by User system December | [6 empty] | LP10
int | string | string | string | Date | Date | string | string | string | float | float | float | float | string | hyperlink | string | float | int | float | hyperlink | string | hyperlink | string | hyperlink | string | string | Date | string | float | float | string | string | float | float | float | string | string | float | float | string | string | string | float | float | float | float | string | string | string | int | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | string | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | string | float | float | float | string | float | float | string | float | string | string | float | float | string | string | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float |  |  | string | float | string | float | float | float | float | float | float | float | float | float | float | float |  | float | float |  |  | string | float |  | float | [5 empty] | float | float | float | float | float | float | float | float |  |  |  | float | float | float | float |  | float | float | float | float | float | int | int | int | float | float | float | int | float | float | float | int | int | float | float | float | float | [18 empty] | float | float | float |  |  | float | float | float |  | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float |  |  | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float
| n/a | n/a | n/a | 2023-12-31 | 2023-12-31 | n/a | n/a | n/a | decimal degrees | decimal degrees | decimal degrees | decimal degrees | n/a | n/a | n/a | square meters | count | kiloWatts | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 2023-12-31 | n/a | MegaWatts | MegaWatts | n/a | n/a | FORMAT?? | n/a | n/a | n/a | n/a | FORMAT?? | FORMAT?? | n/a | n/a | n/a | n/a | n/a | liters per year | FORMAT?? | Yes / No | Yes / No | Yes / No | meters | none | none | none | none | % | MW | MW | MW | MW | MW | kW | Degrees (C) | Degrees (C) | Degrees (C) | Degrees (C) | Degrees (C) | Degrees (C) | Degrees (C) | n/a | bar | bar | bar | Liters per Minute | n/a | n/a | n/a | n/a | Degrees (C) | Degrees (C) | Degrees (C) | Degrees (C) | Degrees (C) | Degrees (C) | Degrees (C) | n/a | bar | bar | Liters per Minute | Yes / No |  |  | Yes / No |  | n/a | Yes / No |  | bar | n/a | n/a | n/a | n/a | kW | n/a | n/a | pflops | [12 empty] | € |  | € | € | € | € | € | € | € | € | € | € | € |  |  | € |  |  | n/a | % |  | years | [5 empty] | € | € | € | € | € | € | € | € |  |  |  | € | € | € | € |  | € | € | € | € | € | mm | m | mm | € | € | € | mm | € | € | € | mm | m | € | € | € | € | [18 empty] | € | € | € | € | € | € | € | € |  | € | € | € | € | € | € | € | € | € | € | € | € | € | € | € | € | € | € | € | € | € | € | € | € |  |  | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | %
A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z | AA | AB | AC | AD | AE | AF | AG | AH | AI | AJ | AK | AL | AM | AN | AO | AP | AQ | AR | AS | AT | AU | AV | AW | AX | AY | AZ | BA | BB | BC | BD | BE | BF | BG | BH | BI | BJ | BK | BL | BM | BN | BO | BP | BQ | BR | BS | BT | BU | BV | BW | BX | BY | BZ | CA | CB | CC | CD | CE | CF | CG | CH | CI | CJ | CK | CL | CM | CN | CO | CP | CQ | CR | CS | CT | CU | CV | CW | CX | CY | CZ | DA | DB | DC | DD | DE | DF | DG | DH | DI | DJ | DK | DL | DM | DN | DO | DP | DQ | DR | DS | DT | DU | DV | DW | DX | DY | DZ | EA | EB | EC | ED | EF | EG | EH | EI | EJ | EK | EL | EM | EN | EO | EP | EQ | ER | ES | ET | EU | EV | EW | EX | EY | EZ | FA | FB | FC | FD | FE | FF | FG | FH | FI | FJ | FK | FL | FM | FN | FO | FP | FQ | FR | FS | FT | FU | FV | FW | FX | FY | FZ | GA | GB | GC | GD | GE | GF | GG | GH | GI | GJ | GK | GL | GM | GN | GO | GP | GQ | GR | GS | GT | GU | GV | GW | GX | GY | GZ |  | HA | HB | HC | HD | HE | HF | HG | HH | HI | HJ | HK | HL | HM | HN | HO | HP | HQ | HR | HS | HT | HU | HV | HW | HX | HY | HZ | IA | IB | IC | ID | IE | IF | IG | IH | II | IJ | IK | IL | IM | IN | IO | IP | IQ | IR | IS | IT | IU | IV | IW | IX | IY | IZ | JA | JB | JC | JD | JE | JF | JG | JH | JI | JJ | JK | JL | JM | JN | JO | JP | JQ | JR | JS | JT | JU | JV | JW | JX | JY | JZ | KA | KB | KC | KD | KE | KF | KG | KH | KI | KJ | KK | KL | KM | KN | KO | KP | KQ | KR | KS | KT | KU | KV | KW | KX | KY | KZ
A: 1 - 5000; B: 50 char; C: 30 char; D: 30 char; E: date; F: date; G: 30 char; H: 30 char; I: 30 char; J: -80.000000 to 80.000000; K: -180.000000 to 180.000000; L: -80.000000 to 80.000000; M: -180.000000 to 180.000000; N: 100 char; O: url; P: 100 char; Q: 100 to 9999; R: 1 to 100000; S: 1 to 300; T: url; U: 100 char; V: url; W: 100 char; X: url; Y: 30 char; Z: 250 char; AA: date; AB: 250 char; AC: 0.0 - 500.0; AD: 0.0 - 500.0; AE: 50 char; AF: 50 char; AI: 0 - 1.0; AJ: 50 char; AK: 50 char; AU: Yes / No; AV: Yes / No; AW: Yes / No; AX: 0 to 5000; AY: 0 <1.0; AZ: 0 <1.0; BA: 0 <1.0; BB: 0 <1.0; BC: 0 <1.0; BD: 0 <1.0; BE: 0.0 to 5000.0; BF: 0.0 to 5000.0; BG: 0.0 to 5000.0; BH: 0.0 to 5000.0; BI: 1.0 - 500.0; BJ: 10.0 - 40.0; BK: 10.0 - 40.0; BL: 10.0 - 40.0; BM: 10.0 - 70.0; BN: 10.0 - 70.0; BO: 10.0 - 70.0; BP: 10.0 - 70.0; BR: 1.0 - 25.0; BS: 1.0 - 25.0; BU: 250 - 10000; BZ: 10.0 - 40.0; CA: 10.0 - 50.0; CB: 10.0 - 50.0; CC: 10.0 - 60.0; CD: 10.0 - 60.0; CE: 10.0 - 60.0; CF: 10.0 - 70.0; CG: 50 char; CH: 1.0 - 25.0; CI: 1.0 - 25.0; CK: Yes / No; CN: Yes / No; CP: 50 char; CQ: Yes / No; CT: 50 char; CU: "Heat Pump", "Boiler"; CV: 0.5 - 1.0; CW: 0.5 - 1.0; CX: 1.0 - 1000.0; CY: (calculated); CZ: (calculated); DB: <1.0; DC: <1.0; DD: <1.0; DE: <1.0; DF: <1.0; DG: <1.0; DH: (calculated); DI: (calculated); DJ: (calculated); DM: 100 char; DN: 0; DO: 100 char; DP: 0; EG: 500 CHAR; EH: 0.001 - 0.10; EJ: .5 - 40.0; FN: (calculated); FO: (calculated); FR: (calculated); FS: (calculated); FT: (calculated) | [27 empty] | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100% | 0 - 100%
index | name | Client | source | date1 | date2 | city | state | country | sitelat | sitelong | userlat | userlong | siteowner | soweblink | ituser | warea | rack | rackkw | itweblink | huowner | howeblink | hruser | huweblink | usertype | relationship | date3 | product | sitepwr | itpwr | pwrsce1 | pwrtype1 | pwrrate1 | pwrrate1ad | pwr1prop | pwrsce2 | pwrtype2 | pwrrate2 | pwrrate2ad | pwrrate2prop | pwralt | pwralttype | pwrratealt | pwrratealtad | h2ouse | h2orate | usebldg | usecamp | useprem | usedist | ere | erf | hre | hrf | hrec | hrfc | wha | uhr | uhrdvrad | hredvrad | pwrf1 | T1min | T1max | T1 | T2min | T2max | T2 | itdt | fluid1 | P2 | P1 | dpit | F1 | fluid1vis | fluid1hc | gwp1 | odp1 | T4min | T4max | T4 | T3min | T3max | T3 | userdt | fluid2 | P4 | P3 | F2 | boost | fluid2vis | fluid2hc | storst | storstsz | storsttyp | storlt | storltsz | dpuser | storlttyp | boosteqp | bsthpcop | bstblreff | pwrf2 | dvrusrday | dvrusryr | datasize | itaircl | itdrcl | itchipcl | itpltcl | it1imm | it2imm | itdivrday | itdvryr | whadvr | n | n | prod1 | prod1rev | prod2 | prod2rev | althtrate | usrpwrrate | benusrcard | benusrmisc | benusremit | benusrnrg | cstusrmnt | cstustext | cstusrsto | cstushteq | n | benitcool | cstitcool | n | n | bounds | r | n | T | n | n | n | n | n | avdemit | avdh20 | heatrev | nrgcerts | avdeqpt | subs | avdemtcst | avdtax | n | n | n | costplan | costperm | costarch | costeng | n | costmjeq | costmneq | cstinslpip | costcntrl | cstelcinst | pipitdia | pipitlen | pipitins | costpipit | costpipe | costanceq | pipusins | costpipusr | costvalit | costvalusr | pipusdia | pipuslen | costcvl | coststct | costinst | costitctr | spaceval | costchlr | costfrec | costmaint | n | n | n | n | n | n | n | n | n | n | n | n | n | n | costproj | costoper | sumoffset | n | n | IRR | NPV | ROI |  | impactyr | impactlif | pric125 | pric140 | pric160 | pric180 | pric200 | pric225 | pric250 | pric280 | pric315 | pric355 | pric400 | prval125 | prval140 | prval160 | prval180 | prval200 | prval225 | prval250 | prval280 | prval315 | prval355 | prval400 |  |  | dvrit00 | dvrit01 | dvrit02 | dvrit03 | dvrit04 | dvrit05 | dvrit06 | dvrit07 | dvrit08 | dvrit09 | dvrit10 | dvrit11 | dvrit12 | dvrit13 | dvrit14 | dvrit15 | dvrit16 | dvrit17 | dvrit18 | dvrit19 | dvrit20 | dvrit21 | dvrit22 | dvrit23 | dvritjan | dvritfeb | dvritmar | dvritapr | dvritmay | dvritjun | dvritjul | dvritaug | dvritsep | dvritoct | dvritnov | dvritdec | dvrusr00 | dvrusr01 | dvrusr02 | dvrusr03 | dvrusr04 | dvrusr05 | dvrusr06 | dvrusr07 | dvrusr08 | dvrusr09 | dvrusr10 | dvrusr11 | dvrusr12 | dvrusr13 | dvrusr14 | dvrusr15 | dvrusr16 | dvrusr17 | dvrusr18 | dvrusr19 | dvrusr20 | dvrusr21 | dvrusr22 | dvrusr23 | dvrusrjan | dvrusrfab | dvrusrmar | dvrusrapr | dvrusrmay | dvrusrjun | dvrusrjul | dvrusraug | dvrusrsep | dvrusroct | dvrusrnov | dvrusrdec | [5 empty] | KZ15
[60 empty] | 557.4495 | #VALUE! | 0 | [5 empty] | 487.7683
[60 empty] | 10452.178 | #VALUE! | 0 | [5 empty] | 8292.0612
[60 empty] | 1811.7109 | #VALUE! | 0 | [5 empty] | 1045.2178
[60 empty] | 5226.089 | #VALUE! | 0 | [5 empty] | 4146.0306
[60 empty] | 3065.9722 | #VALUE! | 0 | [5 empty] | 2508.5227
|  |  | A | n | 1 - 5000 | index | int
|  | n/a | B | n/a | 50 char | name | string
|  | n/a | C | Client | 30 char | Client | string
|  | n/a | D | Client | 30 char | source | string
|  | 2023-12-31 | E | 2023-12-31 | date | date1 | Date
|  | 2023-12-31 | F | 2023-12-31 | date | date2 | Date
|  | n/a | G | n/a | 30 char | city | string
|  | n/a | H | n/a | 30 char | state | string
|  | n/a | I | n/a | 30 char | country | string
|  | decimal degrees | J | n/a | -80.000000 to 80.000000 | sitelat | float
|  | decimal degrees | K | n/a | -180.000000 to 180.000000 | sitelong | float
|  | decimal degrees | L | n/a | -80.000000 to 80.000000 | userlat | float
|  | decimal degrees | M | n/a | -180.000000 to 180.000000 | userlong | float
|  | n/a | N | n/a | 100 char | siteowner | string
|  | n/a | O | n/a | url | soweblink | hyperlink
|  | n/a | P | = siteowner | 100 char | ituser | string
|  | square meters | Q | n/a | 100 to 9999 | warea | float
|  | count | R | n/a | 1 to 100000 | rack | int
|  | kiloWatts | S | n/a | 1 to 300 | rackkw | float
|  | n/a | T | n/a | url | itweblink | hyperlink
|  | n/a | U | n/a | 100 char | huowner | string
|  | n/a | V | n/a | url | howeblink | hyperlink
|  | n/a | W | =huowner | 100 char | hruser | string
|  | n/a | X | n/a | url | huweblink | hyperlink
|  | n/a | Y | SELECTION BOX: | 30 char | usertype | string
|  | n/a | Z | n/a | 250 char | relationship | string
|  | 2023-12-31 | AA | 2023-12-31 | date | date3 | Date
|  | n/a | AB | No | 250 char | product | string
|  | MegaWatts | AC | n/a | 0.0 - 500.0 | sitepwr | float
|  | MegaWatts | AD | n/a | 0.0 - 500.0 | itpwr | float
|  | n/a | AE | n/a | 50 char | pwrsce1 | string
|  | n/a | AF | n/a | 50 char | pwrtype1 | string
|  | FORMAT?? | AG | n/a |  | pwrrate1 | float
|  | n/a | AH | n/a |  | pwrrate1ad | float
|  | n/a | AI | 1 | 0 - 1.0 | pwr1prop | float
|  | n/a | AJ | n/a | 50 char | pwrsce2 | string
|  | n/a | AK | n/a | 50 char | pwrtype2 | string
|  | FORMAT?? | AL | n/a |  | pwrrate2 | float
|  | FORMAT?? | AM | n/a |  | pwrrate2ad | float
|  | n/a | AN | n/a |  | pwrrate2prop | string
|  | n/a | AO | n/a |  | pwralt | string
|  | n/a | AP | n/a |  | pwralttype | string
|  | n/a | AQ | n/a |  | pwrratealt | float
|  | n/a | AR | n/a |  | pwrratealtad | float
|  | liters per year | AS | 0 |  | h2ouse | float
|  | FORMAT?? | AT | 0 |  | h2orate | float
|  | Yes / No | AU | No | Yes / No | usebldg | string
|  | Yes / No | AV | Yes | Yes / No | usecamp | string
|  | Yes / No | AW | Yes | Yes / No | useprem | string
|  | meters | AX | 0 | 0 to 5000 | usedist | int
|  | none | AY |  | 0 <1.0 | ere | float
|  | none | AZ |  | 0 <1.0 | erf | float
|  | none | BA | (calculated) | 0 <1.0 | hre | float
|  | none | BB | (calculated) | 0 <1.0 | hrf | float
|  | % | BC |  | 0 <1.0 | hrec | float
|  | MW | BD |  | 0 <1.0 | hrfc | float
|  | MW | BE | (calculated) | 0.0 to 5000.0 | wha | float
|  | MW | BF | (calculated) | 0.0 to 5000.0 | uhr | float
|  | MW | BG | (calculated) | 0.0 to 5000.0 | uhrdvrad | float
|  | MW | BH | (calculated) | 0.0 to 5000.0 | hredvrad | float
|  | kW | BI | 25 | 1.0 - 500.0 | pwrf1 | float
|  | Degrees (C) | BJ | 10 | 10.0 - 40.0 | T1min | float
|  | Degrees (C) | BK | 40 | 10.0 - 40.0 | T1max | float
|  | Degrees (C) | BL | 30 | 10.0 - 40.0 | T1 | float
|  | Degrees (C) | BM | 20 | 10.0 - 70.0 | T2min | float
|  | Degrees (C) | BN | 60 | 10.0 - 70.0 | T2max | float
|  | Degrees (C) | BO | 40 | 10.0 - 70.0 | T2 | float
|  | Degrees (C) | BP | (calculated) | 10.0 - 70.0 | itdt | float
|  | n/a | BQ | Water |  | fluid1 | string
|  | bar | BR | 4.0 | 1.0 - 25.0 | P2 | float
|  | bar | BS | 1.0 | 1.0 - 25.0 | P1 | float
|  | bar | BT | (calculated) |  | dpit | float
|  | Liters per Minute | BU |  | 250 - 10000 | F1 | float
|  | n/a | BV | n/a |  | fluid1vis | float
|  | n/a | BW | n/a |  | fluid1hc | float
|  | n/a | BX | n/a |  | gwp1 | float
|  | n/a | BY | n/a |  | odp1 | float
|  | Degrees (C) | BZ | 20 | 10.0 - 40.0 | T4min | float
|  | Degrees (C) | CA | 40 | 10.0 - 50.0 | T4max | float
|  | Degrees (C) | CB | 25 | 10.0 - 50.0 | T4 | float
|  | Degrees (C) | CC | 30 | 10.0 - 60.0 | T3min | float
|  | Degrees (C) | CD | 50 | 10.0 - 60.0 | T3max | float
|  | Degrees (C) | CE | 45 | 10.0 - 60.0 | T3 | float
|  | Degrees (C) | CF | (calculated) | 10.0 - 70.0 | userdt | float
|  | n/a | CG | Water | 50 char | fluid2 | string
|  | bar | CH | 5 | 1.0 - 25.0 | P4 | float
|  | bar | CI | 3 | 1.0 - 25.0 | P3 | float
|  | Liters per Minute | CJ |  |  | F2 | float
|  | Yes / No | CK | No | Yes / No | boost | string
|  |  | CL |  |  | fluid2vis | float
|  |  | CM |  |  | fluid2hc | float
|  | Yes / No | CN | No | Yes / No | storst | string
|  |  | CO |  |  | storstsz | float
|  | n/a | CP | Tank | 50 char | storsttyp | string
|  | Yes / No | CQ | No | Yes / No | storlt | string
|  |  | CR |  |  | storltsz | float
|  | bar | CS | (calculated) |  | dpuser | float
|  | n/a | CT | Reservior | 50 char | storlttyp | string
|  | n/a | CU | Heat Pump | "Heat Pump", "Boiler" | boosteqp | string
|  | n/a | CV |  | 0.5 - 1.0 | bsthpcop | float
|  | n/a | CW |  | 0.5 - 1.0 | bstblreff | float
|  | kW | CX | 25 | 1.0 - 1000.0 | pwrf2 | float
|  | n/a | CY | 1 | (calculated) | dvrusrday | float
|  | n/a | CZ | 1 | (calculated) | dvrusryr | float
|  | pflops | DA | n/a |  | datasize | float
|  |  | DB | n/a | <1.0 | itaircl | float
|  |  | DC | n/a | <1.0 | itdrcl | float
|  |  | DD | n/a | <1.0 | itchipcl | float
|  |  | DE | n/a | <1.0 | itpltcl | float
|  |  | DF | n/a | <1.0 | it1imm | float
|  |  | DG | n/a | <1.0 | it2imm | float
|  |  | DH | 1 | (calculated) | itdivrday | float
|  |  | DI | 1 | (calculated) | itdvryr | float
|  |  | DJ | =wha | (calculated) | whadvr | float
|  |  | DK |  |  | n
|  |  | DL |  |  | n
|  |  | DM | No | 100 char | prod1 | string
|  | € | DN | 0 | 0 | prod1rev | float
|  |  | DO | No | 100 char | prod2 | string
|  | € | DP | 0 | 0 | prod2rev | float
|  | € | DQ |  |  | althtrate | float
|  | € | DR |  |  | usrpwrrate | float
|  | € | DS |  |  | benusrcard | float
|  | € | DT |  |  | benusrmisc | float
|  | € | DU |  |  | benusremit | float
|  | € | DV |  |  | benusrnrg | float
|  | € | DW |  |  | cstusrmnt | float
|  | € | DX |  |  | cstustext | float
|  | € | DY |  |  | cstusrsto | float
|  | € | DZ |  |  | cstushteq | float
|  |  | EA |  |  | n
|  |  | EB |  |  | benitcool | float
|  | € | EC |  |  | cstitcool | float
|  |  | ED |  |  | n
|  |  | EF |  |  | n
|  | n/a | EG | HX Flanges | 500 CHAR | bounds | string
|  | % | EH | 0.03 | 0.001 - 0.10 | r | float
|  |  | EI |  |  | n
|  | years | EJ | 20 | .5 - 40.0 | T | float
|  |  | EK |  |  | n
|  |  | EL |  |  | n
|  |  | EM |  |  | n
|  |  | EN |  |  | n
|  |  | EO |  |  | n
|  | € | EP |  |  | avdemit | float
|  | € | EQ |  |  | avdh20 | float
|  | € | ER |  |  | heatrev | float
|  | € | ES |  |  | nrgcerts | float
|  | € | ET |  |  | avdeqpt | float
|  | € | EU |  |  | subs | float
|  | € | EV |  |  | avdemtcst | float
|  | € | EW |  |  | avdtax | float
|  |  | EX |  |  | n
|  |  | EY |  |  | n
|  |  | EZ |  |  | n
|  | € | FA |  |  | costplan | float
|  | € | FB |  |  | costperm | float
|  | € | FC |  |  | costarch | float
|  | € | FD |  |  | costeng | float
|  |  | FE |  |  | n
|  | € | FF |  |  | costmjeq | float
|  | € | FG |  |  | costmneq | float
|  | € | FH |  |  | cstinslpip | float
|  | € | FI |  |  | costcntrl | float
|  | € | FJ |  |  | cstelcinst | float
|  | mm | FK |  |  | pipitdia | int
|  | m | FL |  |  | pipitlen | int
|  | mm | FM |  |  | pipitins | int
|  | € | FN |  | (calculated) | costpipit | float
|  | € | FO | = FN + FR + FS + FT | (calculated) | costpipe | float
|  | € | FP |  |  | costanceq | float
|  | mm | FQ |  |  | pipusins | int
|  | € | FR |  | (calculated) | costpipusr | float
|  | € | FS |  | (calculated) | costvalit | float
|  | € | FT |  | (calculated) | costvalusr | float
|  | mm | FU |  |  | pipusdia | int
|  | m | FV |  |  | pipuslen | int
|  | € | FW |  |  | costcvl | float
|  | € | FX |  |  | coststct | float
|  | € | FY |  |  | costinst | float
|  | € | FZ |  |  | costitctr | float
|  |  | GA |  |  | spaceval
|  |  | GB |  |  | costchlr
|  |  | GC |  |  | costfrec
|  |  | GD |  |  | costmaint
|  |  | GE |  |  | n
|  |  | GF |  |  | n
|  |  | GG |  |  | n
|  |  | GH |  |  | n
|  |  | GI |  |  | n
|  |  | GJ |  |  | n
|  |  | GK |  |  | n
|  |  | GL |  |  | n
|  |  | GM |  |  | n
|  |  | GN |  |  | n
|  |  | GO |  |  | n
|  |  | GP |  |  | n
|  |  | GQ |  |  | n
|  |  | GR |  |  | n
|  | € | GS | (calculated) |  | costproj | float
|  | € | GT | (calculated) |  | costoper | float
|  | € | GU | (calculated) |  | sumoffset | float
|  | € | GV | (calculated) |  | n
|  | € | GW | (calculated) |  | n
|  | € | GX | (calculated) |  | IRR | float
|  | € | GY | (calculated) |  | NPV | float
|  | € | GZ | (calculated) |  | ROI | float
|  | € | HA | (calculated) |  | impactyr | float
|  | € | HB | (calculated) |  | impactlif | float
|  | € | HC | (calculated) |  | pric125 | float
|  | € | HD | (calculated) |  | pric140 | float
|  | € | HE | (calculated) |  | pric160 | float
|  | € | HF | (calculated) |  | pric180 | float
|  | € | HG | (calculated) |  | pric200 | float
|  | € | HH | (calculated) |  | pric225 | float
|  | € | HI | (calculated) |  | pric250 | float
|  | € | HJ | (calculated) |  | pric280 | float
|  | € | HK | (calculated) |  | pric315 | float
|  | € | HL | (calculated) |  | pric355 | float
|  | € | HM | (calculated) |  | pric400 | float
|  | € | HN | (calculated) |  | prval125 | float
|  | € | HO | (calculated) |  | prval140 | float
|  | € | HP | (calculated) |  | prval160 | float
|  | € | HQ | (calculated) |  | prval180 | float
|  | € | HR | (calculated) |  | prval200 | float
|  | € | HS | (calculated) |  | prval225 | float
|  | € | HT | (calculated) |  | prval250 | float
|  | € | HU | (calculated) |  | prval280 | float
|  | € | HV | (calculated) |  | prval315 | float
|  | € | HW | (calculated) |  | prval355 | float
|  | € | HX | (calculated) |  | prval400 | float
HY
HZ
|  | % | IA | 100% | 0 - 100% | dvrit00 | float
|  | % | IB | 100% | 0 - 100% | dvrit01 | float
|  | % | IC | 100% | 0 - 100% | dvrit02 | float
|  | % | ID | 100% | 0 - 100% | dvrit03 | float
|  | % | IE | 100% | 0 - 100% | dvrit04 | float
|  | % | IF | 100% | 0 - 100% | dvrit05 | float
|  | % | IG | 100% | 0 - 100% | dvrit06 | float
|  | % | IH | 100% | 0 - 100% | dvrit07 | float
|  | % | II | 100% | 0 - 100% | dvrit08 | float
|  | % | IJ | 100% | 0 - 100% | dvrit09 | float
|  | % | IK | 100% | 0 - 100% | dvrit10 | float
|  | % | IL | 100% | 0 - 100% | dvrit11 | float
|  | % | IM | 100% | 0 - 100% | dvrit12 | float
|  | % | IN | 100% | 0 - 100% | dvrit13 | float
|  | % | IO | 100% | 0 - 100% | dvrit14 | float
|  | % | IP | 100% | 0 - 100% | dvrit15 | float
|  | % | IQ | 100% | 0 - 100% | dvrit16 | float
|  | % | IR | 100% | 0 - 100% | dvrit17 | float
|  | % | IS | 100% | 0 - 100% | dvrit18 | float
|  | % | IT | 100% | 0 - 100% | dvrit19 | float
|  | % | IU | 100% | 0 - 100% | dvrit20 | float
|  | % | IV | 100% | 0 - 100% | dvrit21 | float
|  | % | IW | 100% | 0 - 100% | dvrit22 | float
|  | % | IX | 100% | 0 - 100% | dvrit23 | float
|  | % | IY | 100% | 0 - 100% | dvritjan | float
|  | % | IZ | 100% | 0 - 100% | dvritfeb | float
|  | % | JA | 100% | 0 - 100% | dvritmar | float
|  | % | JB | 100% | 0 - 100% | dvritapr | float
|  | % | JC | 100% | 0 - 100% | dvritmay | float
|  | % | JD | 100% | 0 - 100% | dvritjun | float
|  | % | JE | 100% | 0 - 100% | dvritjul | float
|  | % | JF | 100% | 0 - 100% | dvritaug | float
|  | % | JG | 100% | 0 - 100% | dvritsep | float
|  | % | JH | 100% | 0 - 100% | dvritoct | float
|  | % | JI | 100% | 0 - 100% | dvritnov | float
|  | % | JJ | 100% | 0 - 100% | dvritdec | float
|  | % | JK | 100% | 0 - 100% | dvrusr00 | float
|  | % | JL | 100% | 0 - 100% | dvrusr01 | float
|  | % | JM | 100% | 0 - 100% | dvrusr02 | float
|  | % | JN | 100% | 0 - 100% | dvrusr03 | float
|  | % | JO | 100% | 0 - 100% | dvrusr04 | float
|  | % | JP | 100% | 0 - 100% | dvrusr05 | float
|  | % | JQ | 100% | 0 - 100% | dvrusr06 | float
|  | % | JR | 100% | 0 - 100% | dvrusr07 | float
|  | % | JS | 100% | 0 - 100% | dvrusr08 | float
|  | % | JT | 100% | 0 - 100% | dvrusr09 | float
|  | % | JU | 100% | 0 - 100% | dvrusr10 | float
|  | % | JV | 100% | 0 - 100% | dvrusr11 | float
|  | % | JW | 100% | 0 - 100% | dvrusr12 | float
|  | % | JX | 100% | 0 - 100% | dvrusr13 | float
|  | % | JY | 100% | 0 - 100% | dvrusr14 | float
|  | % | JZ | 100% | 0 - 100% | dvrusr15 | float
|  | % | KA | 100% | 0 - 100% | dvrusr16 | float
|  | % | KB | 100% | 0 - 100% | dvrusr17 | float
|  | % | KC | 100% | 0 - 100% | dvrusr18 | float
|  | % | KD | 100% | 0 - 100% | dvrusr19 | float
|  | % | KE | 100% | 0 - 100% | dvrusr20 | float
|  | % | KF | 100% | 0 - 100% | dvrusr21 | float
|  | % | KG | 100% | 0 - 100% | dvrusr22 | float
|  | % | KH | 100% | 0 - 100% | dvrusr23 | float
|  | % | KI | 100% | 0 - 100% | dvrusrjan | float
|  | % | KJ | 100% | 0 - 100% | dvrusrfab | float
|  | % | KK | 100% | 0 - 100% | dvrusrmar | float
|  | % | KL | 100% | 0 - 100% | dvrusrapr | float
|  | % | KM | 100% | 0 - 100% | dvrusrmay | float
|  | % | KN | 100% | 0 - 100% | dvrusrjun | float
|  | % | KO | 100% | 0 - 100% | dvrusrjul | float
|  | % | KP | 100% | 0 - 100% | dvrusraug | float
|  | % | KQ | 100% | 0 - 100% | dvrusrsep | float
|  | % | KR | 100% | 0 - 100% | dvrusroct | float
|  | % | KS | 100% | 0 - 100% | dvrusrnov | float
|  | % | KT | 100% | 0 - 100% | dvrusrdec | float
KU
KV
KW
KX
KY
KZ

## PIPE
Pipe Size | Sch 40 | Stainless
0.5 |  |  |  | Imaginary Room Size
0.75 |  |  |  | MW | P | "A" | "L"
1 |  |  |  | 1 | 8 | 56 | 12.4833
1.5 |  |  |  | 2 | 10 | 63 | 12.9373
2 | 71.3416 | 356.7078 |  | 3 | 12 | 99 | 14.9499
2.5 | 89.1769 | 445.8847 |  | 5 | 16 | 187 | 18.6748
3 | 107.0123 | 535.0617
4 | 142.6831 | 713.4156
5 | 178.3539 | 891.7695
6 | 214.0247 | 2508.9 | PER 20
8 | 285.4 | 1427 | PER 2
10 | 356.7078 | 1783.539
12 | 428.0494 | 2140.2468
14 | 499.3909 | 2496.9546
16 | 570.7325 | 2853.6624
18 | 642.074 | 3210.3702
20 | 713.4156 | 3567.078
24 | 856.0987 | 4280.4936
30 | 1070.1234 | 5350.617

## PUMPS
DATA TO COME IN THE FUTURE

## INSTRUMENTS (hidden)
DATA COMING SOON

## FTGS ETC
Pipe Size | Bolts for 150# Flanges | FLANGES | flange - 316 | T.O.L. | Elbows
1/2 |  | 23.76 | 45.56 | 74.94
3/4 |  | 25.15 | 60.09 | 74.94
1 | 4~1/2"-13 UNC x 3" Long | 30.52 | 70.47 |  | 34.28
1 1/2 | 4~1/2"-13 UNC x 3.5" Long | 33.19 | 89.45 |  | 34.86
2 | 4~5/8"-11 UNC x 3.5" Long | 31.96 | 104.83 |  | 35.89
2 1/2 | 4~5/8"-11 UNC x 4" Long | 40.17 | 185.65 |  | 57.29
3 | 4~5/8"-11 UNC x 4" Long | 40.76 | 209.91 |  | 67.18
4 | 8~5/8"-11 UNC x 4" Long | 58.75 | 254.57 |  | 88.34
5 | 8~3/4"-10 UNC x 4.5" Long | 71.75 | 325 |  | 175
6 | 8~3/4"-10 UNC x 4.5" Long | 85.36 | 429.62 |  | 225.1
8 | 8~3/4"-10 UNC x 5" Long | 137.42 | 728.27 |  | 355.72
10 | 12~7/8"-9 UNC x 5.5" Long | 160.25 | 800
12 | 12~7/8"-9 UNC x 5.5" Long | 263.38 | 919.48
14 | 12~1"-8 UNC x 6" Long | 308 | 1540
16 | 16~1"-8 UNC x 6" Long | 352 | 1760
18 | 16~1 1/8"-7 UNC x 6.5" Long | 396 | 1980
20 | 20~1 1/8"-7 UNC x 7" Long | 440 | 2200
24 | 20~1 1/8"-7 UNC x 7 1/2" | 528 | 2640
30 | 20~1 1/4"-7 UNC x 7.5" Long | 660 | 3300